## Scenarios
scenario | wind_mw | pv_mw | storage_mwh | start_storage_mwh | backup_limit_pct | annual_load_mwh | wind_generation_mwh | pv_generation_mwh | storage_generation_mwh | storage_pumping_mwh | biodiesel_backup_generation_mwh | backup_share_pct | overproduction_mwh | lcoe_eur_per_kwh | residual_load_1_not_met_mwh | residual_load_2_not_met_mwh | max_biodiesel_capacity_mw | max_pump_mw | max_storage_generation_mw | feasible_against_limit | obvious_constraint_or_failure
A | 40 | 100 | 450 | 225 | 5 | 320824 | 191041.4104 | 204953.8311 | 51071.5367 | 66694.3693 | 15153.4624 | 4.7233 | 63758.5706 | 0.092869 | 65147.3431 | 15153.4624 | 40.6657 | 81.0187 | 46.0434 | TRUE | No obvious first-pass failure
B | 55 | 70 | 450 | 225 | 5 | 320824 | 262681.9392 | 143467.6818 | 29131.4456 | 37642.7133 | 22016.3804 | 6.8624 | 84748.6768 | 0.092543 | 50179.3055 | 22016.3804 | 45.8697 | 71.8386 | 45.0309 | FALSE | Biodiesel share exceeds scenario backup limit
C | 30 | 125 | 450 | 225 | 5 | 320824 | 143281.0578 | 256192.2889 | 76940.7879 | 101282.5795 | 9316.2684 | 2.9039 | 54154.3488 | 0.094598 | 85167.1227 | 9316.2684 | 37.2053 | 95.5803 | 46.1593 | TRUE | No obvious first-pass failure
D | 40 | 100 | 700 | 350 | 2.5 | 320824 | 191041.4104 | 204953.8311 | 54602.6055 | 71818.6683 | 11377.8509 | 3.5464 | 59320.9276 | 0.096025 | 65147.3431 | 11377.8509 | 40.6657 | 81.7847 | 46.0434 | FALSE | Biodiesel share exceeds scenario backup limit
E | 40 | 100 | 250 | 125 | 5 | 320824 | 191041.4104 | 204953.8311 | 45326.8036 | 58329.697 | 21416.6834 | 6.6755 | 71002.3768 | 0.093001 | 65147.3431 | 21416.6834 | 40.6657 | 81.0187 | 46.0434 | FALSE | Biodiesel share exceeds scenario backup limit

## Metadata
item | value
Load source | Santiago calibrated proxy load from Cabo Verde calibrated national shape
Weather source | NASA POWER Hourly API fallback after Renewables.ninja 2023 rejection
Representative point | Praia, Santiago Island, Cabo Verde (14.92, -23.51)
Wind full-load-equivalent hours from workbook probe | 4776.0353
PV full-load-equivalent hours from workbook probe | 2049.5383
Moderate storage rule | 450.0 MWh (~12 hours of average Santiago load)
Best of A-C | A
Best overall first-pass scenario | A