## Line Data
Line ID | From | To | Type | Parallel | Length [km] | Resistance [Ohm] | Reactance [Ohm]
1 | 2 | 11 | E | 1 | 0.5 | 0.0625 | 0.0485
2 | 4 | 5 | E | 1 | 0.1 | 0.0125 | 0.0097
3 | 5 | 6 | G | 1 | 0.6 | 0.2322 | 0.0792
4 | 11 | 12 | E | 6 | 0.3 | 0.225 | 0.1746
5 | 12 | 15 | E | 1 | 1.1 | 0.1375 | 0.1067
6 | 12 | 42 | E | 1 | 8.3 | 1.0375 | 0.8051
7 | 12 | 45 | E | 1 | 8.7 | 1.0875 | 0.8439
8 | 15 | 16 | E | 1 | 1.7 | 0.2125 | 0.1649
9 | 15 | 17 | E | 1 | 1 | 0.125 | 0.097
10 | 15 | 19 | C | 1 | 0.9 | 0.2277 | 0.1017
11 | 12 | 21 | E | 1 | 0.56 | 0.07 | 0.05432
12 | 17 | 18 | G | 1 | 0.8 | 0.3096 | 0.1056
13 | 18 | 19 | G | 1 | 0.7 | 0.2709 | 0.0924
14 | 16 | 20 | E | 1 | 0.5 | 0.0625 | 0.0485
15 | 20 | 21 | E | 1 | 0.2 | 0.025 | 0.0194
16 | 21 | 22 | E | 1 | 0.3 | 0.0375 | 0.0291
17 | 15 | 26 | E | 1 | 0.5 | 0.0625 | 0.0485
18 | 15 | 23 | E | 1 | 1.4 | 0.175 | 0.1358
19 | 23 | 24 | C | 1 | 0.4 | 0.1012 | 0.0452
20 | 24 | 25 | G | 1 | 0.6 | 0.2322 | 0.0792
21 | 25 | 27 | C | 1 | 0.5 | 0.1265 | 0.0565
22 | 22 | 26 | E | 1 | 0.5 | 0.0625 | 0.0485
23 | 26 | 27 | E | 1 | 2 | 0.25 | 0.194
24 | 26 | 28 | C | 1 | 0.8 | 0.2024 | 0.0904
25 | 26 | 30 | G | 1 | 1 | 0.387 | 0.132
26 | 26 | 32 | G | 1 | 0.75 | 0.29025 | 0.099
27 | 26 | 33 | G | 1 | 0.9 | 0.3483 | 0.1188
28 | 26 | 35 | H | 1 | 0.8 | 0.1544 | 0.0952
29 | 28 | 29 | C | 1 | 0.5 | 0.1265 | 0.0565
30 | 29 | 21 | C | 1 | 0.75 | 0.18975 | 0.08475
31 | 29 | 34 | G | 1 | 0.4 | 0.1548 | 0.0528
32 | 29 | 47 | E | 1 | 1 | 0.125 | 0.097
33 | 30 | 31 | G | 1 | 0.9 | 0.3483 | 0.1188
34 | 31 | 32 | G | 1 | 0.8 | 0.3096 | 0.1056
35 | 33 | 34 | C | 1 | 0.7 | 0.1771 | 0.0791
36 | 27 | 35 | H | 1 | 0.36 | 0.06948 | 0.04284
37 | 27 | 36 | G | 1 | 0.5 | 0.1935 | 0.066
38 | 27 | 38 | G | 1 | 0.5 | 0.1935 | 0.066
39 | 27 | 39 | C | 1 | 0.5 | 0.1265 | 0.0565
40 | 27 | 45 | E | 1 | 1.65 | 0.20625 | 0.16005
41 | 27 | 41 | C | 1 | 1.2 | 0.3036 | 0.1356
42 | 36 | 37 | G | 1 | 0.7 | 0.2709 | 0.0924
43 | 37 | 38 | G | 1 | 0.7 | 0.2709 | 0.0924
44 | 39 | 40 | C | 1 | 0.5 | 0.1265 | 0.0565
45 | 40 | 41 | C | 1 | 0.5 | 0.1265 | 0.0565
48 | 41 | 42 | C | 1 | 0.5 | 0.1265 | 0.0565
49 | 42 | 43 | G | 1 | 0.7 | 0.2709 | 0.0924
50 | 43 | 44 | G | 1 | 0.8 | 0.3096 | 0.1056
51 | 42 | 49 | E | 1 | 0.6 | 0.075 | 0.0582
52 | 49 | 50 | E | 1 | 1.4 | 0.175 | 0.1358
53 | 45 | 46 | E | 1 | 0.4 | 0.05 | 0.0388
54 | 46 | 47 | E | 1 | 1.9 | 0.2375 | 0.1843
55 | 47 | 48 | E | 1 | 1.2 | 0.15 | 0.1164
56 | 48 | 50 | E | 1 | 2.7 | 0.3375 | 0.2619
57 | 48 | 51 | E | 1 | 0.7 | 0.0875 | 0.0679
58 | 51 | 52 | E | 1 | 2 | 0.25 | 0.194
59 | 48 | 56 | E | 1 | 5 | 0.625 | 0.485
60 | 45 | 56 | E | 1 | 4 | 0.5 | 0.388
61 | 45 | 54 | G | 1 | 1 | 0.387 | 0.132
62 | 54 | 55 | G | 1 | 0.7 | 0.2709 | 0.0924
63 | 53 | 55 | G | 1 | 0.9 | 0.3483 | 0.1188
64 | 45 | 53 | G | 1 | 2 | 0.774 | 0.264
65 | 56 | 60 | E | 1 | 2 | 0.25 | 0.194
66 | 60 | 61 | E | 1 | 0.7 | 0.0875 | 0.0679
67 | 61 | 64 | G | 1 | 1 | 0.387 | 0.132
68 | 64 | 65 | G | 1 | 4 | 1.548 | 0.528
69 | 61 | 62 | G | 1 | 2.8 | 1.0836 | 0.3696
70 | 62 | 63 | G | 1 | 1 | 0.387 | 0.132
71 | 62 | 66 | G | 1 | 1.2 | 0.4644 | 0.1584
72 | 66 | 67 | C | 1 | 0.7 | 0.1771 | 0.0791
73 | 13 | 57 | F | 1 | 12 | 1.752 | 4.8
74 | 14 | 68 | F | 1 | 38 | 5.548 | 15.2
75 | 58 | 69 | F | 1 | 32 | 4.672 | 12.8
76 | 70 | 71 | E | 1 | 0.25 | 0.03125 | 0.02425
77 | 70 | 106 | E | 1 | 0.2 | 0.025 | 0.0194
78 | 74 | 106 | E | 1 | 12 | 1.5 | 1.164
79 | 76 | 106 | E | 1 | 20 | 2.5 | 1.94
80 | 70 | 77 | E | 1 | 17 | 2.125 | 1.649
81 | 70 | 78 | E | 1 | 2.4 | 0.3 | 0.2328
82 | 78 | 79 | E | 1 | 2 | 0.25 | 0.194
83 | 78 | 80 | E | 1 | 0.7 | 0.0875 | 0.0679
84 | 80 | 81 | E | 1 | 2.5 | 0.3125 | 0.2425
85 | 81 | 82 | E | 1 | 3 | 0.375 | 0.291
86 | 82 | 83 | E | 1 | 0.7 | 0.0875 | 0.0679
87 | 83 | 84 | E | 1 | 0.5 | 0.0625 | 0.0485
88 | 84 | 85 | E | 1 | 0.5 | 0.0625 | 0.0485
89 | 77 | 83 | E | 1 | 0.3 | 0.0375 | 0.0291
90 | 77 | 87 | E | 1 | 1 | 0.125 | 0.097
91 | 85 | 87 | E | 1 | 0.7 | 0.0875 | 0.0679
92 | 85 | 86 | E | 1 | 0.85 | 0.10625 | 0.08245
93 | 77 | 88 | G | 1 | 0.3 | 0.1161 | 0.0396
94 | 71 | 72 | E | 1 | 0.4 | 0.05 | 0.0388
95 | 72 | 73 | E | 1 | 0.32 | 0.04 | 0.03104
96 | 73 | 74 | E | 1 | 2 | 0.25 | 0.194
97 | 74 | 89 | E | 1 | 0.7 | 0.0875 | 0.0679
98 | 89 | 90 | E | 1 | 0.3 | 0.0375 | 0.0291
99 | 90 | 91 | E | 1 | 0.3 | 0.0375 | 0.0291
100 | 91 | 92 | E | 1 | 0.25 | 0.03125 | 0.02425
101 | 90 | 92 | E | 1 | 0.6 | 0.075 | 0.0582
102 | 74 | 93 | E | 1 | 1.3 | 0.1625 | 0.1261
103 | 93 | 94 | E | 1 | 0.7 | 0.0875 | 0.0679
104 | 94 | 95 | E | 1 | 1.5 | 0.1875 | 0.1455
105 | 72 | 75 | E | 1 | 10 | 1.25 | 0.97
106 | 75 | 76 | E | 1 | 1 | 0.125 | 0.097
107 | 76 | 98 | E | 1 | 0.5 | 0.0625 | 0.0485
108 | 76 | 103 | E | 1 | 0.75 | 0.09375 | 0.07275
109 | 98 | 99 | E | 1 | 0.6 | 0.075 | 0.0582
110 | 99 | 100 | G | 1 | 0.25 | 0.09675 | 0.033
111 | 100 | 101 | G | 1 | 0.3 | 0.1161 | 0.0396
112 | 101 | 102 | G | 1 | 0.4 | 0.1548 | 0.0528
113 | 99 | 102 | G | 1 | 0.3 | 0.1161 | 0.0396
114 | 101 | 103 | G | 1 | 0.25 | 0.09675 | 0.033
115 | 103 | 104 | E | 1 | 0.5 | 0.0625 | 0.0485
116 | 104 | 105 | E | 1 | 0.35 | 0.04375 | 0.03395
117 | 76 | 105 | E | 1 | 0.4 | 0.05 | 0.0388
118 | 1 | 2 | TB | 1 | 0 | 80 | 0.56
119 | 3 | 4 | TB | 1 | 0 | 80 | 0.56
120 | 7 | 11 | TE | 1 | 0 | 26.6667 | 0.13867
121 | 8 | 11 | TF | 1 | 0 | 16 | 0.065766
122 | 9 | 11 | TF | 1 | 0 | 16 | 0.065766
123 | 10 | 11 | TF | 1 | 0 | 16 | 0.065766
124 | 11 | 13 | TH | 1 | 0 | 163.6364 | 0.86727
125 | 11 | 14 | TH | 1 | 0 | 163.6364 | 0.86727
126 | 56 | 57 | TH | 1 | 0 | 163.6364 | 0.86727
127 | 56 | 58 | TH | 1 | 0 | 163.6364 | 0.86727
128 | 56 | 59 | TE | 1 | 0 | 26.6667 | 0.13867
129 | 68 | 70 | TG | 1 | 0 | 300 | 1.83
130 | 69 | 70 | TG | 1 | 0 | 300 | 1.83
131 | 76 | 96 | TB | 1 | 0 | 80 | 0.56
132 | 76 | 97 | TA | 1 | 0 | 400 | 3.84

## Conductors
Type ID | Material | Cross section [mm2] | Vrating | R [Ω/km] | X [Ω/km] | C [nF/km] | Nominal Rating [kA] | SCCR [kA] | Type | FRI [failure/(year*km)]
A | Al | 50 | 20 kV | 0.6042 | 0.117 | 9.9 | 0.225 | 3.5 | OHL | 0.022
B | Al | 70 | 20 kV | 0.433 | 0.1225 | 220 | 0.204 | 6.6 | UG | 0.02
C | Al | 120 | 20 kV | 0.253 | 0.113 | 260 | 0.277 | 11.3 | UG | 0.018
D | Al | 185 | 20 kV | 0.164 | 0.1068 | 310 | 0.352 | 17.5 | UG | 0.021
E | Al | 240 | 20 kV | 0.125 | 0.097 | 340 | 0.408 | 22.7 | UG | 0.02
F | Al | 400 | 60 kV | 0.146 | 0.4 | 10 | 0.3 | 6 | OHL | 0.022
G | Cu | 50 | 20 kV | 0.387 | 0.132 | 190 | 0.214 | 7.2 | UG | 0.018
H | Cu | 95 | 20 kV | 0.193 | 0.119 | 230 | 0.313 | 13.6 | UG | 0.017
R [Ω/km] - Resistence
X [Ω/km] - Reactance
C [nF/km] - Capacitance
UG - Underground
OHL - Over Head Line
FRI - Failure Rate Index

## Transformers
Type ID | Power [MVA] | Vrating [kV] | R1pu | X1pu | R0pu | X0pu | X/R [%] | Zb | R1 Ohm | X1 Ohm
TA | 1 | 20/0.4 | 0.0096 | 0.059227 | 0.0096 | 0.059227 | 5 | 400 | 3.84 | 23.6908
TB | 5 | 20/0.4 | 0.007 | 0.069649 | 0.007 | 0.069649 | 6 | 80 | 0.56 | 5.5719
TC | 7 | 20/0.4 | 0.0064267 | 0.079741 | 0.0064267 | 0.079741 | 8.06 | 57.1429 | 0.36724 | 4.5567
TD | 10 | 20/0.6 | 0.0068 | 0.07971 | 0.0068 | 0.07971 | 9.1 | 40 | 0.272 | 3.1884
TE | 15 | 20/10 | 0.0052 | 0.08985 | 0.0052 | 0.08985 | 9.08 | 26.6667 | 0.13867 | 2.396
TF | 25 | 20/10 | 0.0041104 | 0.10292 | 0 | 0.09 | 6.99 | 16 | 0.065766 | 1.6467
TG | 12 | 60/20 | 0.0061 | 0.082511 | 0.0061 | 0.082511 | 8.47 | 300 | 1.83 | 24.7533
TH | 22 | 60/20 | 0.0053 | 0.099859 | 0.0053 | 0.099859 | 7.71 | 163.6364 | 0.86727 | 16.3406

## Load Data
Bus ID | Pbase [MW] | Qbase [MVAr] | Controllable [MW] | Critical [MW] | Controllable [%] | Critical [%] | % of Total | % of Control | % of Critical | 0.9 | PF | cos(phi) | 0.9
6 | 2.5 | 1.2108 | 2.375 | 0.125 | 95 | 5 | 2.7917 | 2.6521 | 0.13959 |  | 0.9 | P | 5 | 5
16 | 1.6 | 0.77492 | 0 | 0 | 0 | 0 | 1.7867 | 0 | 0 |  | 0.9 | Q | 2.4216 | 0.073743 | 2.2007
17 | 1.5 | 0.72648 | 0 | 0 | 0 | 0 | 1.675 | 0 | 0 |  | 0.9 | S | 5.4629
18 | 2.2 | 1.0655 | 0.55 | 0 | 25 | 0 | 2.4567 | 0.61418 | 0 |  | 0.9 | pf | 0.91527
19 | 2 | 0.96864 | 0 | 0 | 0 | 0 | 2.2334 | 0 | 0 |  | 0.9 | pf | 0.9
20 | 1.6 | 0.77492 | 0 | 0 | 0 | 0 | 1.7867 | 0 | 0 |  | 0.9
22 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
23 | 1.8 | 0.87178 | 0 | 0.18 | 0 | 10 | 2.0101 | 0 | 0.20101 |  | 0.9
24 | 1.2 | 0.58119 | 0 | 0.18 | 0 | 15 | 1.34 | 0 | 0.20101 |  | 0.9
25 | 0.9 | 0.43589 | 0 | 0.108 | 0 | 12 | 1.005 | 0 | 0.1206 |  | 0.9
28 | 1.2 | 0.58119 | 0 | 0.18 | 0 | 15 | 1.34 | 0 | 0.20101 |  | 0.9
30 | 1.2 | 0.58119 | 0 | 0.12 | 0 | 10 | 1.34 | 0 | 0.134 |  | 0.9
31 | 2 | 0.96864 | 0 | 0.24 | 0 | 12 | 2.2334 | 0 | 0.26801 |  | 0.9
32 | 2 | 0.96864 | 0 | 0.2 | 0 | 10 | 2.2334 | 0 | 0.22334 |  | 0.9
33 | 1.4 | 0.67805 | 0 | 0 | 0 | 0 | 1.5634 | 0 | 0 |  | 0.9
34 | 2.2 | 1.0655 | 0.011 | 0 | 0.5 | 0 | 2.4567 | 0.012284 | 0 |  | 0.9
35 | 2.6 | 1.2592 | 0.013 | 0 | 0.5 | 0 | 2.9034 | 0.014517 | 0 |  | 0.9
36 | 2 | 0.96864 | 0 | 0 | 0 | 0 | 2.2334 | 0 | 0 |  | 0.9
37 | 2 | 0.96864 | 0 | 0 | 0 | 0 | 2.2334 | 0 | 0 |  | 0.9
38 | 3 | 1.453 | 0 | 0 | 0 | 0 | 3.3501 | 0 | 0 |  | 0.9
39 | 2.2 | 1.0655 | 0 | 0 | 0 | 0 | 2.4567 | 0 | 0 |  | 0.9
40 | 3 | 1.453 | 0 | 0 | 0 | 0 | 3.3501 | 0 | 0 |  | 0.9
41 | 2 | 0.96864 | 0 | 0 | 0 | 0 | 2.2334 | 0 | 0 |  | 0.9
43 | 3.1 | 1.5014 | 0 | 0 | 0 | 0 | 3.4618 | 0 | 0 |  | 0.9
44 | 2.1 | 1.0171 | 0 | 0 | 0 | 0 | 2.3451 | 0 | 0 |  | 0.9
46 | 4 | 1.9373 | 0.8 | 0.4 | 20 | 10 | 4.4668 | 0.89336 | 0.44668 |  | 0.9
47 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
49 | 2.2 | 1.0655 | 0 | 0.44 | 0 | 20 | 2.4567 | 0 | 0.49135 |  | 0.9
50 | 2.2 | 1.0655 | 0 | 0.22 | 0 | 10 | 2.4567 | 0 | 0.24567 |  | 0.9
51 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
52 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
53 | 0.8 | 0.38746 | 0 | 0.08 | 0 | 10 | 0.89336 | 0 | 0.089336 |  | 0.9
54 | 2.2 | 1.0655 | 0.88 | 0 | 40 | 0 | 2.4567 | 0.98269 | 0 |  | 0.9
55 | 3 | 1.453 | 0 | 0.3 | 0 | 10 | 3.3501 | 0 | 0.33501 |  | 0.9
60 | 2 | 0.96864 | 0.6 | 0 | 30 | 0 | 2.2334 | 0.67002 | 0 |  | 0.9
63 | 1 | 0.48432 | 0 | 0.1 | 0 | 10 | 1.1167 | 0 | 0.11167 |  | 0.9
64 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
65 | 0.2 | 0.096864 | 0 | 0 | 0 | 0 | 0.22334 | 0 | 0 |  | 0.9
66 | 0.2 | 0.096864 | 0 | 0 | 0 | 0 | 0.22334 | 0 | 0 |  | 0.9
67 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
71 | 0.3 | 0.1453 | 0 | 0 | 0 | 0 | 0.33501 | 0 | 0 |  | 0.9
73 | 0.3 | 0.1453 | 0 | 0 | 0 | 0 | 0.33501 | 0 | 0 |  | 0.9
75 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
78 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
79 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
80 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
81 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
82 | 0.3 | 0.1453 | 0 | 0 | 0 | 0 | 0.33501 | 0 | 0 |  | 0.9
84 | 0.8 | 0.38746 | 0 | 0 | 0 | 0 | 0.89336 | 0 | 0 |  | 0.9
86 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
87 | 0.6 | 0.29059 | 0 | 0 | 0 | 0 | 0.67002 | 0 | 0 |  | 0.9
88 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
89 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
90 | 1.1 | 0.53275 | 0 | 0 | 0 | 0 | 1.2284 | 0 | 0 |  | 0.9
91 | 1.5 | 0.72648 | 0 | 0 | 0 | 0 | 1.675 | 0 | 0 |  | 0.9
92 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
93 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
94 | 0.7 | 0.33903 | 0 | 0 | 0 | 0 | 0.78169 | 0 | 0 |  | 0.9
95 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
98 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
99 | 2.2 | 1.0655 | 1.76 | 0 | 80 | 0 | 2.4567 | 1.9654 | 0 |  | 0.9
100 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9
101 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
102 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
103 | 0.9 | 0.43589 | 0 | 0 | 0 | 0 | 1.005 | 0 | 0 |  | 0.9
104 | 0.25 | 0.12108 | 0 | 0 | 0 | 0 | 0.27917 | 0 | 0 |  | 0.9
105 | 0.5 | 0.24216 | 0 | 0 | 0 | 0 | 0.55835 | 0 | 0 |  | 0.9
Total | 89.55 | 43.371 | 6.989 | 2.873 | 291 | 159 | 100

## Load Data Reduced
Bus ID | Pbase [MW] | Qbase [MVAr] | Controllable [MW] | Critical [MW] | Controllable [%] | Critical [%] | % of Total | % of Control | % of Critical | 0.9 | PF | cos(phi) | 0.9
5 | 2.5 | 1.2108 | 2.375 | 0.125 | 95 | 5 | 2.7917 | 2.6521 | 0.13959 |  | 0.9 | P | 5 | 5
15 | 5.7 | 2.7606 | 0.55 | 0 | 9.6491 | 0 | 6.3652 | 0.61418 | 0 |  | 0.9 | Q | 2.4216 | 0.073743 | 2.2007
20 | 3.2 | 1.5498 | 0 | 0 | 0 | 0 | 3.5734 | 0 | 0 |  | 0.9 | S | 5.4629
24 | 3.9 | 1.8889 | 0 | 0.468 | 0 | 12 | 4.3551 | 0 | 0.52261 |  | 0.9 | pf | 0.91527
26 | 1 | 0.48432 | 0 | 0 | 0 | 0 | 1.1167 | 0 | 0 |  | 0.9 | pf | 0.9
28 | 1.2 | 0.58119 | 0 | 0.18 | 0 | 15 | 1.34 | 0 | 0.20101 |  | 0.9
31 | 5.2 | 2.5185 | 0 | 0.56 | 0 | 10.7692 | 5.8068 | 0 | 0.62535 |  | 0.9
34 | 3.6 | 1.7436 | 0.011 | 0 | 0.30556 | 0 | 4.0201 | 0.012284 | 0 |  | 0.9
35 | 2.6 | 1.2592 | 0.013 | 0 | 0.5 | 0 | 2.9034 | 0.014517 | 0 |  | 0.9
37 | 7 | 3.3903 | 0 | 0 | 0 | 0 | 7.8169 | 0 | 0 |  | 0.9
40 | 5.2 | 2.5185 | 0 | 0 | 0 | 0 | 5.8068 | 0 | 0 |  | 0.9
41 | 2 | 0.96864 | 0 | 0 | 0 | 0 | 2.2334 | 0 | 0 |  | 0.9
44 | 5.2 | 2.5185 | 0 | 0 | 0 | 0 | 5.8068 | 0 | 0 |  | 0.9
47 | 5 | 2.4216 | 0.8 | 0.4 | 20 | 10 | 5.5835 | 1.1167 | 0.55835 |  | 0.9
48 | 6.4 | 3.0997 | 0 | 0.66 | 0 | 10.3125 | 7.1468 | 0 | 0.73702 |  | 0.9
55 | 6 | 2.9059 | 0.88 | 0.38 | 14.6667 | 6.3333 | 6.7002 | 0.98269 | 0.42434 |  | 0.9
56 | 4.4 | 2.131 | 0.6 | 0.1 | 13.6364 | 2.2727 | 4.9135 | 0.67002 | 0.11167 |  | 0.9
71 | 1.1 | 0.53275 | 0 | 0 | 0 | 0 | 1.2284 | 0 | 0 |  | 0.9
86 | 5.2 | 2.5185 | 0 | 0 | 0 | 0 | 5.8068 | 0 | 0 |  | 0.9
95 | 6.3 | 3.0512 | 0 | 0 | 0 | 0 | 7.0352 | 0 | 0 |  | 0.9
98 | 3.7 | 1.792 | 1.76 | 0 | 47.5676 | 0 | 4.1318 | 1.9654 | 0 |  | 0.9
100 | 3.15 | 1.5256 | 0 | 0 | 0 | 0 | 3.5176 | 0 | 0 |  | 0.9
Total | 89.55 | 43.371 | 6.989 | 2.873 | 201.3253 | 71.6878 | 100

## Weekly Load Profile
Month | Week | % of Base
1 | 1 | 90.5
1 | 2 | 99.8
1 | 3 | 93.4
1 | 4 | 94.5
2 | 5 | 94.5
2 | 6 | 97.8
2 | 7 | 98
2 | 8 | 99.8
3 | 9 | 99.6
3 | 10 | 99.6
3 | 11 | 99.1
3 | 12 | 100
4 | 13 | 99.1
4 | 14 | 97.4
4 | 15 | 93.2
4 | 16 | 89
5 | 17 | 87
5 | 18 | 85
5 | 19 | 83.7
5 | 20 | 87.4
6 | 21 | 87.4
6 | 22 | 85.7
6 | 23 | 87.6
6 | 24 | 89.6
7 | 25 | 84.3
7 | 26 | 85
7 | 27 | 83.2
7 | 28 | 78.6
8 | 29 | 76.6
8 | 30 | 76.2
8 | 31 | 72.4
8 | 32 | 75.1
8 | 33 | 77.5
9 | 34 | 79.2
9 | 35 | 81.2
9 | 36 | 81.9
9 | 37 | 82.3
9 | 38 | 83
10 | 39 | 82.8
10 | 40 | 85.9
10 | 41 | 88.5
10 | 42 | 90.3
10 | 43 | 90.5
11 | 44 | 91.2
11 | 45 | 90.3
11 | 46 | 88.7
11 | 47 | 87
11 | 48 | 88.1
12 | 49 | 89.8
12 | 50 | 89.8
12 | 51 | 95.7
12 | 52 | 90.5

## Daily Load Profile
ID | Name | % of base
1 | Moday | 94.2
2 | Tuesday | 98.1
3 | Wednesday | 95.6
4 | Thursday | 100
5 | Friday | 97.5
6 | Saturday | 76.3
7 | Sunday | 73.9

## Seasonal Load Profile
Hours |  | 0-1 | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10-11 | 11-12 | 12-13 | 13-14 | 14-15 | 15-16 | 16-17 | 17-18 | 18-19 | 19-20 | 20-21 | 21-22 | 22-23 | 23-24
Winter - weeks 49-08 | Weekday | 80 | 75 | 78 | 80 | 83 | 86 | 89 | 90 | 92 | 95 | 94 | 96 | 96 | 94 | 90 | 90 | 93 | 96 | 100 | 100 | 99 | 94 | 84 | 83
| Weekend | 72 | 67.5 | 70.2 | 72 | 74.7 | 77.4 | 80.1 | 81 | 82.8 | 85.5 | 84.6 | 86.4 | 86.4 | 84.6 | 81 | 81 | 83.7 | 86.4 | 90 | 90 | 89.1 | 84.6 | 75.6 | 74.7
Spring - weeks 09-22 | Weekday | 86 | 86 | 84 | 83 | 84 | 84 | 87 | 90 | 95 | 98 | 99 | 98 | 96 | 92 | 89 | 87 | 90 | 95 | 99 | 100 | 99 | 97 | 90 | 93
| Weekend | 79.12 | 79.12 | 77.28 | 76.36 | 77.28 | 77.28 | 80.04 | 82.8 | 87.4 | 90.16 | 91.08 | 90.16 | 88.32 | 84.64 | 81.88 | 80.04 | 82.8 | 87.4 | 91.08 | 92 | 91.08 | 89.24 | 82.8 | 85.56
Summer - weeks 23-35 | Weekday | 81 | 77 | 80 | 79 | 82 | 84 | 87 | 90 | 94 | 95 | 94 | 93 | 91 | 88 | 87 | 91 | 95 | 98 | 100 | 97 | 94 | 84 | 88 | 91
| Weekend | 76.95 | 73.15 | 76 | 75.05 | 77.9 | 79.8 | 82.65 | 85.5 | 89.3 | 90.25 | 89.3 | 88.35 | 86.45 | 83.6 | 82.65 | 86.45 | 90.25 | 93.1 | 95 | 92.15 | 89.3 | 79.8 | 83.6 | 86.45
Autum - weeks 36-48 | Weekday | 80 | 81 | 82 | 84 | 86 | 86 | 89 | 90 | 92 | 94 | 96 | 95 | 94 | 92 | 90 | 90 | 92 | 100 | 100 | 100 | 97 | 93 | 83 | 83
| Weekend | 70.4 | 71.28 | 72.16 | 73.92 | 75.68 | 75.68 | 78.32 | 79.2 | 80.96 | 82.72 | 84.48 | 83.6 | 82.72 | 80.96 | 79.2 | 79.2 | 80.96 | 88 | 88 | 88 | 85.36 | 81.84 | 73.04 | 73.04

## Hourly Load Profile
Hourly Load Profile assuming Mon-Fri
Hours
Month | Week | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
1 | 1 | 72.4 | 67.9 | 70.6 | 72.4 | 75.1 | 77.8 | 80.5 | 81.4 | 83.3 | 86 | 85.1 | 86.9 | 86.9 | 85.1 | 81.4 | 81.4 | 84.2 | 86.9 | 90.5 | 90.5 | 89.6 | 85.1 | 76 | 75.1
1 | 2 | 79.8 | 74.8 | 77.8 | 79.8 | 82.8 | 85.8 | 88.8 | 89.8 | 91.8 | 94.8 | 93.8 | 95.8 | 95.8 | 93.8 | 89.8 | 89.8 | 92.8 | 95.8 | 99.8 | 99.8 | 98.8 | 93.8 | 83.8 | 82.8
1 | 3 | 74.7 | 70 | 72.9 | 74.7 | 77.5 | 80.3 | 83.1 | 84.1 | 85.9 | 88.7 | 87.8 | 89.7 | 89.7 | 87.8 | 84.1 | 84.1 | 86.9 | 89.7 | 93.4 | 93.4 | 92.5 | 87.8 | 78.5 | 77.5
1 | 4 | 75.6 | 70.9 | 73.7 | 75.6 | 78.4 | 81.3 | 84.1 | 85 | 86.9 | 89.8 | 88.8 | 90.7 | 90.7 | 88.8 | 85 | 85 | 87.9 | 90.7 | 94.5 | 94.5 | 93.6 | 88.8 | 79.4 | 78.4
1 | 5 | 75.6 | 70.9 | 73.7 | 75.6 | 78.4 | 81.3 | 84.1 | 85 | 86.9 | 89.8 | 88.8 | 90.7 | 90.7 | 88.8 | 85 | 85 | 87.9 | 90.7 | 94.5 | 94.5 | 93.6 | 88.8 | 79.4 | 78.4
2 | 6 | 78.2 | 73.4 | 76.3 | 78.2 | 81.2 | 84.1 | 87 | 88 | 90 | 92.9 | 91.9 | 93.9 | 93.9 | 91.9 | 88 | 88 | 91 | 93.9 | 97.8 | 97.8 | 96.8 | 91.9 | 82.2 | 81.2
2 | 7 | 78.4 | 73.5 | 76.4 | 78.4 | 81.3 | 84.3 | 87.2 | 88.2 | 90.2 | 93.1 | 92.1 | 94.1 | 94.1 | 92.1 | 88.2 | 88.2 | 91.1 | 94.1 | 98 | 98 | 97 | 92.1 | 82.3 | 81.3
2 | 8 | 79.8 | 74.8 | 77.8 | 79.8 | 82.8 | 85.8 | 88.8 | 89.8 | 91.8 | 94.8 | 93.8 | 95.8 | 95.8 | 93.8 | 89.8 | 89.8 | 92.8 | 95.8 | 99.8 | 99.8 | 98.8 | 93.8 | 83.8 | 82.8
3 | 9 | 85.7 | 85.7 | 83.7 | 82.7 | 83.7 | 83.7 | 86.7 | 89.6 | 94.6 | 97.6 | 98.6 | 97.6 | 95.6 | 91.6 | 88.6 | 86.7 | 89.6 | 94.6 | 98.6 | 99.6 | 98.6 | 96.6 | 89.6 | 92.6
3 | 10 | 85.7 | 85.7 | 83.7 | 82.7 | 83.7 | 83.7 | 86.7 | 89.6 | 94.6 | 97.6 | 98.6 | 97.6 | 95.6 | 91.6 | 88.6 | 86.7 | 89.6 | 94.6 | 98.6 | 99.6 | 98.6 | 96.6 | 89.6 | 92.6
3 | 11 | 85.2 | 85.2 | 83.2 | 82.3 | 83.2 | 83.2 | 86.2 | 89.2 | 94.1 | 97.1 | 98.1 | 97.1 | 95.1 | 91.2 | 88.2 | 86.2 | 89.2 | 94.1 | 98.1 | 99.1 | 98.1 | 96.1 | 89.2 | 92.2
3 | 12 | 86 | 86 | 84 | 83 | 84 | 84 | 87 | 90 | 95 | 98 | 99 | 98 | 96 | 92 | 89 | 87 | 90 | 95 | 99 | 100 | 99 | 97 | 90 | 93
3 | 13 | 85.2 | 85.2 | 83.2 | 82.3 | 83.2 | 83.2 | 86.2 | 89.2 | 94.1 | 97.1 | 98.1 | 97.1 | 95.1 | 91.2 | 88.2 | 86.2 | 89.2 | 94.1 | 98.1 | 99.1 | 98.1 | 96.1 | 89.2 | 92.2
4 | 14 | 83.8 | 83.8 | 81.8 | 80.8 | 81.8 | 81.8 | 84.7 | 87.7 | 92.5 | 95.5 | 96.4 | 95.5 | 93.5 | 89.6 | 86.7 | 84.7 | 87.7 | 92.5 | 96.4 | 97.4 | 96.4 | 94.5 | 87.7 | 90.6
4 | 15 | 80.2 | 80.2 | 78.3 | 77.4 | 78.3 | 78.3 | 81.1 | 83.9 | 88.5 | 91.3 | 92.3 | 91.3 | 89.5 | 85.7 | 82.9 | 81.1 | 83.9 | 88.5 | 92.3 | 93.2 | 92.3 | 90.4 | 83.9 | 86.7
4 | 16 | 76.5 | 76.5 | 74.8 | 73.9 | 74.8 | 74.8 | 77.4 | 80.1 | 84.6 | 87.2 | 88.1 | 87.2 | 85.4 | 81.9 | 79.2 | 77.4 | 80.1 | 84.6 | 88.1 | 89 | 88.1 | 86.3 | 80.1 | 82.8
4 | 17 | 74.8 | 74.8 | 73.1 | 72.2 | 73.1 | 73.1 | 75.7 | 78.3 | 82.6 | 85.3 | 86.1 | 85.3 | 83.5 | 80 | 77.4 | 75.7 | 78.3 | 82.6 | 86.1 | 87 | 86.1 | 84.4 | 78.3 | 80.9
5 | 18 | 73.1 | 73.1 | 71.4 | 70.6 | 71.4 | 71.4 | 74 | 76.5 | 80.8 | 83.3 | 84.2 | 83.3 | 81.6 | 78.2 | 75.6 | 74 | 76.5 | 80.8 | 84.2 | 85 | 84.2 | 82.4 | 76.5 | 79
5 | 19 | 72 | 72 | 70.3 | 69.5 | 70.3 | 70.3 | 72.8 | 75.3 | 79.5 | 82 | 82.9 | 82 | 80.4 | 77 | 74.5 | 72.8 | 75.3 | 79.5 | 82.9 | 83.7 | 82.9 | 81.2 | 75.3 | 77.8
5 | 20 | 75.2 | 75.2 | 73.4 | 72.5 | 73.4 | 73.4 | 76 | 78.7 | 83 | 85.7 | 86.5 | 85.7 | 83.9 | 80.4 | 77.8 | 76 | 78.7 | 83 | 86.5 | 87.4 | 86.5 | 84.8 | 78.7 | 81.3
5 | 21 | 75.2 | 75.2 | 73.4 | 72.5 | 73.4 | 73.4 | 76 | 78.7 | 83 | 85.7 | 86.5 | 85.7 | 83.9 | 80.4 | 77.8 | 76 | 78.7 | 83 | 86.5 | 87.4 | 86.5 | 84.8 | 78.7 | 81.3
5 | 22 | 73.7 | 73.7 | 72 | 71.1 | 72 | 72 | 74.6 | 77.1 | 81.4 | 84 | 84.8 | 84 | 82.3 | 78.8 | 76.3 | 74.6 | 77.1 | 81.4 | 84.8 | 85.7 | 84.8 | 83.1 | 77.1 | 79.7
6 | 23 | 71 | 67.5 | 70.1 | 69.2 | 71.8 | 73.6 | 76.2 | 78.8 | 82.3 | 83.2 | 82.3 | 81.5 | 79.7 | 77.1 | 76.2 | 79.7 | 83.2 | 85.8 | 87.6 | 85 | 82.3 | 73.6 | 77.1 | 79.7
6 | 24 | 72.6 | 69 | 71.7 | 70.8 | 73.5 | 75.3 | 78 | 80.6 | 84.2 | 85.1 | 84.2 | 83.3 | 81.5 | 78.8 | 78 | 81.5 | 85.1 | 87.8 | 89.6 | 86.9 | 84.2 | 75.3 | 78.8 | 81.5
6 | 25 | 68.3 | 64.9 | 67.4 | 66.6 | 69.1 | 70.8 | 73.3 | 75.9 | 79.2 | 80.1 | 79.2 | 78.4 | 76.7 | 74.2 | 73.3 | 76.7 | 80.1 | 82.6 | 84.3 | 81.8 | 79.2 | 70.8 | 74.2 | 76.7
6 | 26 | 68.8 | 65.4 | 68 | 67.2 | 69.7 | 71.4 | 74 | 76.5 | 79.9 | 80.8 | 79.9 | 79 | 77.4 | 74.8 | 74 | 77.4 | 80.8 | 83.3 | 85 | 82.4 | 79.9 | 71.4 | 74.8 | 77.4
7 | 27 | 67.4 | 64.1 | 66.6 | 65.7 | 68.2 | 69.9 | 72.4 | 74.9 | 78.2 | 79 | 78.2 | 77.4 | 75.7 | 73.2 | 72.4 | 75.7 | 79 | 81.5 | 83.2 | 80.7 | 78.2 | 69.9 | 73.2 | 75.7
7 | 28 | 63.7 | 60.5 | 62.9 | 62.1 | 64.5 | 66 | 68.4 | 70.7 | 73.9 | 74.7 | 73.9 | 73.1 | 71.5 | 69.2 | 68.4 | 71.5 | 74.7 | 77 | 78.6 | 76.2 | 73.9 | 66 | 69.2 | 71.5
7 | 29 | 62 | 59 | 61.3 | 60.5 | 62.8 | 64.3 | 66.6 | 68.9 | 72 | 72.8 | 72 | 71.2 | 69.7 | 67.4 | 66.6 | 69.7 | 72.8 | 75.1 | 76.6 | 74.3 | 72 | 64.3 | 67.4 | 69.7
7 | 30 | 61.7 | 58.7 | 61 | 60.2 | 62.5 | 64 | 66.3 | 68.6 | 71.6 | 72.4 | 71.6 | 70.9 | 69.3 | 67.1 | 66.3 | 69.3 | 72.4 | 74.7 | 76.2 | 73.9 | 71.6 | 64 | 67.1 | 69.3
8 | 31 | 58.6 | 55.7 | 57.9 | 57.2 | 59.4 | 60.8 | 63 | 65.2 | 68.1 | 68.8 | 68.1 | 67.3 | 65.9 | 63.7 | 63 | 65.9 | 68.8 | 71 | 72.4 | 70.2 | 68.1 | 60.8 | 63.7 | 65.9
8 | 32 | 60.8 | 57.8 | 60.1 | 59.3 | 61.6 | 63.1 | 65.3 | 67.6 | 70.6 | 71.3 | 70.6 | 69.8 | 68.3 | 66.1 | 65.3 | 68.3 | 71.3 | 73.6 | 75.1 | 72.8 | 70.6 | 63.1 | 66.1 | 68.3
8 | 33 | 62.8 | 59.7 | 62 | 61.2 | 63.6 | 65.1 | 67.4 | 69.8 | 72.8 | 73.6 | 72.8 | 72.1 | 70.5 | 68.2 | 67.4 | 70.5 | 73.6 | 76 | 77.5 | 75.2 | 72.8 | 65.1 | 68.2 | 70.5
8 | 34 | 64.2 | 61 | 63.4 | 62.6 | 64.9 | 66.5 | 68.9 | 71.3 | 74.4 | 75.2 | 74.4 | 73.7 | 72.1 | 69.7 | 68.9 | 72.1 | 75.2 | 77.6 | 79.2 | 76.8 | 74.4 | 66.5 | 69.7 | 72.1
8 | 35 | 65.8 | 62.5 | 65 | 64.1 | 66.6 | 68.2 | 70.6 | 73.1 | 76.3 | 77.1 | 76.3 | 75.5 | 73.9 | 71.5 | 70.6 | 73.9 | 77.1 | 79.6 | 81.2 | 78.8 | 76.3 | 68.2 | 71.5 | 73.9
9 | 36 | 65.5 | 66.3 | 67.2 | 68.8 | 70.4 | 70.4 | 72.9 | 73.7 | 75.3 | 77 | 78.6 | 77.8 | 77 | 75.3 | 73.7 | 73.7 | 75.3 | 81.9 | 81.9 | 81.9 | 79.4 | 76.2 | 68 | 68
9 | 37 | 65.8 | 66.7 | 67.5 | 69.1 | 70.8 | 70.8 | 73.2 | 74.1 | 75.7 | 77.4 | 79 | 78.2 | 77.4 | 75.7 | 74.1 | 74.1 | 75.7 | 82.3 | 82.3 | 82.3 | 79.8 | 76.5 | 68.3 | 68.3
9 | 38 | 66.4 | 67.2 | 68.1 | 69.7 | 71.4 | 71.4 | 73.9 | 74.7 | 76.4 | 78 | 79.7 | 78.8 | 78 | 76.4 | 74.7 | 74.7 | 76.4 | 83 | 83 | 83 | 80.5 | 77.2 | 68.9 | 68.9
9 | 39 | 66.2 | 67.1 | 67.9 | 69.6 | 71.2 | 71.2 | 73.7 | 74.5 | 76.2 | 77.8 | 79.5 | 78.7 | 77.8 | 76.2 | 74.5 | 74.5 | 76.2 | 82.8 | 82.8 | 82.8 | 80.3 | 77 | 68.7 | 68.7
10 | 40 | 68.7 | 69.6 | 70.4 | 72.2 | 73.9 | 73.9 | 76.5 | 77.3 | 79 | 80.7 | 82.5 | 81.6 | 80.7 | 79 | 77.3 | 77.3 | 79 | 85.9 | 85.9 | 85.9 | 83.3 | 79.9 | 71.3 | 71.3
10 | 41 | 70.8 | 71.7 | 72.6 | 74.3 | 76.1 | 76.1 | 78.8 | 79.6 | 81.4 | 83.2 | 85 | 84.1 | 83.2 | 81.4 | 79.6 | 79.6 | 81.4 | 88.5 | 88.5 | 88.5 | 85.8 | 82.3 | 73.5 | 73.5
10 | 42 | 72.2 | 73.1 | 74 | 75.9 | 77.7 | 77.7 | 80.4 | 81.3 | 83.1 | 84.9 | 86.7 | 85.8 | 84.9 | 83.1 | 81.3 | 81.3 | 83.1 | 90.3 | 90.3 | 90.3 | 87.6 | 84 | 74.9 | 74.9
10 | 43 | 72.4 | 73.3 | 74.2 | 76 | 77.8 | 77.8 | 80.5 | 81.4 | 83.3 | 85.1 | 86.9 | 86 | 85.1 | 83.3 | 81.4 | 81.4 | 83.3 | 90.5 | 90.5 | 90.5 | 87.8 | 84.2 | 75.1 | 75.1
10 | 44 | 73 | 73.9 | 74.8 | 76.6 | 78.4 | 78.4 | 81.2 | 82.1 | 83.9 | 85.7 | 87.6 | 86.6 | 85.7 | 83.9 | 82.1 | 82.1 | 83.9 | 91.2 | 91.2 | 91.2 | 88.5 | 84.8 | 75.7 | 75.7
11 | 45 | 72.2 | 73.1 | 74 | 75.9 | 77.7 | 77.7 | 80.4 | 81.3 | 83.1 | 84.9 | 86.7 | 85.8 | 84.9 | 83.1 | 81.3 | 81.3 | 83.1 | 90.3 | 90.3 | 90.3 | 87.6 | 84 | 74.9 | 74.9
11 | 46 | 71 | 71.8 | 72.7 | 74.5 | 76.3 | 76.3 | 78.9 | 79.8 | 81.6 | 83.4 | 85.2 | 84.3 | 83.4 | 81.6 | 79.8 | 79.8 | 81.6 | 88.7 | 88.7 | 88.7 | 86 | 82.5 | 73.6 | 73.6
11 | 47 | 69.6 | 70.5 | 71.3 | 73.1 | 74.8 | 74.8 | 77.4 | 78.3 | 80 | 81.8 | 83.5 | 82.6 | 81.8 | 80 | 78.3 | 78.3 | 80 | 87 | 87 | 87 | 84.4 | 80.9 | 72.2 | 72.2
11 | 48 | 70.5 | 71.4 | 72.2 | 74 | 75.8 | 75.8 | 78.4 | 79.3 | 81.1 | 82.8 | 84.6 | 83.7 | 82.8 | 81.1 | 79.3 | 79.3 | 81.1 | 88.1 | 88.1 | 88.1 | 85.5 | 81.9 | 73.1 | 73.1
12 | 49 | 71.8 | 67.4 | 70 | 71.8 | 74.5 | 77.2 | 79.9 | 80.8 | 82.6 | 85.3 | 84.4 | 86.2 | 86.2 | 84.4 | 80.8 | 80.8 | 83.5 | 86.2 | 89.8 | 89.8 | 88.9 | 84.4 | 75.4 | 74.5
12 | 50 | 71.8 | 67.4 | 70 | 71.8 | 74.5 | 77.2 | 79.9 | 80.8 | 82.6 | 85.3 | 84.4 | 86.2 | 86.2 | 84.4 | 80.8 | 80.8 | 83.5 | 86.2 | 89.8 | 89.8 | 88.9 | 84.4 | 75.4 | 74.5
12 | 51 | 76.6 | 71.8 | 74.6 | 76.6 | 79.4 | 82.3 | 85.2 | 86.1 | 88 | 90.9 | 90 | 91.9 | 91.9 | 90 | 86.1 | 86.1 | 89 | 91.9 | 95.7 | 95.7 | 94.7 | 90 | 80.4 | 79.4
12 | 52 | 72.4 | 67.9 | 70.6 | 72.4 | 75.1 | 77.8 | 80.5 | 81.4 | 83.3 | 86 | 85.1 | 86.9 | 86.9 | 85.1 | 81.4 | 81.4 | 84.2 | 86.9 | 90.5 | 90.5 | 89.6 | 85.1 | 76 | 75.1

## Equivalent Week Profile Load
Month | Day | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Original
1 | 1 | 71.2529 | 66.7996 | 69.4716 | 71.2529 | 73.9249 | 76.5968 | 79.2688 | 80.1595 | 81.9408 | 84.6128 | 83.7221 | 85.5035 | 85.5035 | 83.7221 | 80.1595 | 80.1595 | 82.8315 | 85.5035 | 89.0661 | 89.0661 | 88.1754 | 83.7221 | 74.8155 | 73.9249 | 1
1 | 2 | 74.2028 | 69.5652 | 72.3478 | 74.2028 | 76.9854 | 79.7681 | 82.5507 | 83.4782 | 85.3333 | 88.1159 | 87.1883 | 89.0434 | 89.0434 | 87.1883 | 83.4782 | 83.4782 | 86.2608 | 89.0434 | 92.7536 | 92.7536 | 91.826 | 87.1883 | 77.913 | 76.9854 | 1
1 | 3 | 72.3118 | 67.7924 | 70.504 | 72.3118 | 75.0235 | 77.7352 | 80.4469 | 81.3508 | 83.1586 | 85.8703 | 84.9664 | 86.7742 | 86.7742 | 84.9664 | 81.3508 | 81.3508 | 84.0625 | 86.7742 | 90.3898 | 90.3898 | 89.4859 | 84.9664 | 75.9274 | 75.0235
1 | 4 | 75.64 | 70.9125 | 73.749 | 75.64 | 78.4765 | 81.313 | 84.1495 | 85.095 | 86.986 | 89.8225 | 88.877 | 90.768 | 90.768 | 88.877 | 85.095 | 85.095 | 87.9315 | 90.768 | 94.55 | 94.55 | 93.6045 | 88.877 | 79.422 | 78.4765 | 1
1 | 5 | 73.749 | 69.1397 | 71.9053 | 73.749 | 76.5146 | 79.2802 | 82.0458 | 82.9676 | 84.8114 | 87.5769 | 86.6551 | 88.4988 | 88.4988 | 86.6551 | 82.9676 | 82.9676 | 85.7332 | 88.4988 | 92.1863 | 92.1863 | 91.2644 | 86.6551 | 77.4365 | 76.5146
1 | 6 | 51.942 | 48.6956 | 50.6434 | 51.942 | 53.8898 | 55.8376 | 57.7855 | 58.4347 | 59.7333 | 61.6811 | 61.0318 | 62.3304 | 62.3304 | 61.0318 | 58.4347 | 58.4347 | 60.3826 | 62.3304 | 64.9275 | 64.9275 | 64.2782 | 61.0318 | 54.5391 | 53.8898 | 1
1 | 7 | 50.3082 | 47.1639 | 49.0505 | 50.3082 | 52.1947 | 54.0813 | 55.9678 | 56.5967 | 57.8544 | 59.7409 | 59.1121 | 60.3698 | 60.3698 | 59.1121 | 56.5967 | 56.5967 | 58.4832 | 60.3698 | 62.8852 | 62.8852 | 62.2564 | 59.1121 | 52.8236 | 52.1947 | 1
2 | 8 | 73.4948 | 68.9014 | 71.6575 | 73.4948 | 76.2509 | 79.007 | 81.763 | 82.6817 | 84.5191 | 87.2751 | 86.3564 | 88.1938 | 88.1938 | 86.3564 | 82.6817 | 82.6817 | 85.4378 | 88.1938 | 91.8686 | 91.8686 | 90.9499 | 86.3564 | 77.1696 | 76.2509
2 | 9 | 76.5376 | 71.754 | 74.6242 | 76.5376 | 79.4078 | 82.2779 | 85.1481 | 86.1048 | 88.0183 | 90.8884 | 89.9317 | 91.8451 | 91.8451 | 89.9317 | 86.1048 | 86.1048 | 88.975 | 91.8451 | 95.672 | 95.672 | 94.7153 | 89.9317 | 80.3645 | 79.4078 | 2
2 | 10 | 74.5871 | 69.9254 | 72.7224 | 74.5871 | 77.3841 | 80.1812 | 82.9782 | 83.9105 | 85.7752 | 88.5722 | 87.6399 | 89.5045 | 89.5045 | 87.6399 | 83.9105 | 83.9105 | 86.7075 | 89.5045 | 93.2339 | 93.2339 | 92.3016 | 87.6399 | 78.3165 | 77.3841
2 | 11 | 78.02 | 73.1437 | 76.0695 | 78.02 | 80.9458 | 83.8715 | 86.7973 | 87.7725 | 89.723 | 92.6488 | 91.6735 | 93.624 | 93.624 | 91.6735 | 87.7725 | 87.7725 | 90.6983 | 93.624 | 97.525 | 97.525 | 96.5498 | 91.6735 | 81.921 | 80.9458 | 2
2 | 12 | 76.0695 | 71.3152 | 74.1678 | 76.0695 | 78.9221 | 81.7747 | 84.6273 | 85.5782 | 87.4799 | 90.3325 | 89.3817 | 91.2834 | 91.2834 | 89.3817 | 85.5782 | 85.5782 | 88.4308 | 91.2834 | 95.0869 | 95.0869 | 94.136 | 89.3817 | 79.873 | 78.9221
2 | 13 | 53.5763 | 50.2278 | 52.2369 | 53.5763 | 55.5854 | 57.5946 | 59.6037 | 60.2734 | 61.6128 | 63.6219 | 62.9522 | 64.2916 | 64.2916 | 62.9522 | 60.2734 | 60.2734 | 62.2825 | 64.2916 | 66.9704 | 66.9704 | 66.3007 | 62.9522 | 56.2552 | 55.5854 | 2
2 | 14 | 51.8911 | 48.6479 | 50.5938 | 51.8911 | 53.837 | 55.7829 | 57.7289 | 58.3775 | 59.6748 | 61.6207 | 60.972 | 62.2693 | 62.2693 | 60.972 | 58.3775 | 58.3775 | 60.3234 | 62.2693 | 64.8639 | 64.8639 | 64.2152 | 60.972 | 54.4857 | 53.837
3 | 15 | 80.6677 | 80.6677 | 78.7917 | 77.8537 | 78.7917 | 78.7917 | 81.6057 | 84.4197 | 89.1097 | 91.9237 | 92.8617 | 91.9237 | 90.0477 | 86.2957 | 83.4817 | 81.6057 | 84.4197 | 89.1097 | 92.8617 | 93.7996 | 92.8617 | 90.9857 | 84.4197 | 87.2337 | 3
3 | 16 | 84.0074 | 84.0074 | 82.0538 | 81.077 | 82.0538 | 82.0538 | 84.9843 | 87.9148 | 92.7989 | 95.7294 | 96.7062 | 95.7294 | 93.7758 | 89.8684 | 86.9379 | 84.9843 | 87.9148 | 92.7989 | 96.7062 | 97.6831 | 96.7062 | 94.7526 | 87.9148 | 90.8453 | 3
3 | 17 | 81.8666 | 81.8666 | 79.9627 | 79.0108 | 79.9627 | 79.9627 | 82.8185 | 85.6743 | 90.434 | 93.2898 | 94.2418 | 93.2898 | 91.386 | 87.5782 | 84.7224 | 82.8185 | 85.6743 | 90.434 | 94.2418 | 95.1937 | 94.2418 | 92.3379 | 85.6743 | 88.5301
3 | 18 | 85.6345 | 85.6345 | 83.643 | 82.6472 | 83.643 | 83.643 | 86.6302 | 89.6175 | 94.5962 | 97.5835 | 98.5792 | 97.5835 | 95.592 | 91.609 | 88.6217 | 86.6302 | 89.6175 | 94.5962 | 98.5792 | 99.575 | 98.5792 | 96.5877 | 89.6175 | 92.6047 | 3
3 | 19 | 83.4936 | 83.4936 | 81.5519 | 80.5811 | 81.5519 | 81.5519 | 84.4645 | 87.3771 | 92.2313 | 95.1439 | 96.1148 | 95.1439 | 93.2022 | 89.3188 | 86.4062 | 84.4645 | 87.3771 | 92.2313 | 96.1148 | 97.0856 | 96.1148 | 94.1731 | 87.3771 | 90.2896
3 | 20 | 60.112 | 60.112 | 58.714 | 58.0151 | 58.714 | 58.714 | 60.811 | 62.9079 | 66.4028 | 68.4997 | 69.1987 | 68.4997 | 67.1018 | 64.3059 | 62.2089 | 60.811 | 62.9079 | 66.4028 | 69.1987 | 69.8977 | 69.1987 | 67.8007 | 62.9079 | 65.0048 | 3
3 | 21 | 58.2212 | 58.2212 | 56.8672 | 56.1902 | 56.8672 | 56.8672 | 58.8982 | 60.9291 | 64.3141 | 66.3451 | 67.0221 | 66.3451 | 64.9911 | 62.2831 | 60.2522 | 58.8982 | 60.9291 | 64.3141 | 67.0221 | 67.6991 | 67.0221 | 65.6681 | 60.9291 | 62.9601 | 3
4 | 22 | 76.6981 | 76.6981 | 74.9144 | 74.0226 | 74.9144 | 74.9144 | 77.5899 | 80.2655 | 84.7247 | 87.4002 | 88.292 | 87.4002 | 85.6165 | 82.0491 | 79.3736 | 77.5899 | 80.2655 | 84.7247 | 88.292 | 89.1839 | 88.292 | 86.5083 | 80.2655 | 82.941 | 4
4 | 23 | 79.8735 | 79.8735 | 78.016 | 77.0872 | 78.016 | 78.016 | 80.8023 | 83.5886 | 88.2324 | 91.0187 | 91.9474 | 91.0187 | 89.1611 | 85.4461 | 82.6598 | 80.8023 | 83.5886 | 88.2324 | 91.9474 | 92.8762 | 91.9474 | 90.0899 | 83.5886 | 86.3748
4 | 24 | 77.838 | 77.838 | 76.0278 | 75.1227 | 76.0278 | 76.0278 | 78.7431 | 81.4584 | 85.9838 | 88.6991 | 89.6042 | 88.6991 | 86.8889 | 83.2686 | 80.5533 | 78.7431 | 81.4584 | 85.9838 | 89.6042 | 90.5093 | 89.6042 | 87.794 | 81.4584 | 84.1736 | 4
4 | 25 | 81.4205 | 81.4205 | 79.527 | 78.5803 | 79.527 | 79.527 | 82.3672 | 85.2075 | 89.9412 | 92.7815 | 93.7283 | 92.7815 | 90.888 | 87.101 | 84.2608 | 82.3672 | 85.2075 | 89.9412 | 93.7283 | 94.675 | 93.7283 | 91.8347 | 85.2075 | 88.0477
4 | 26 | 79.385 | 79.385 | 77.5388 | 76.6157 | 77.5388 | 77.5388 | 80.3081 | 83.0773 | 87.6927 | 90.462 | 91.385 | 90.462 | 88.6158 | 84.9235 | 82.1542 | 80.3081 | 83.0773 | 87.6927 | 91.385 | 92.3081 | 91.385 | 89.5389 | 83.0773 | 85.8466 | 4
4 | 27 | 57.1539 | 57.1539 | 55.8248 | 55.1602 | 55.8248 | 55.8248 | 57.8185 | 59.8123 | 63.1352 | 65.1289 | 65.7935 | 65.1289 | 63.7997 | 61.1414 | 59.1477 | 57.8185 | 59.8123 | 63.1352 | 65.7935 | 66.4581 | 65.7935 | 64.4643 | 59.8123 | 61.806
4 | 28 | 55.3562 | 55.3562 | 54.0688 | 53.4251 | 54.0688 | 54.0688 | 55.9998 | 57.9309 | 61.1493 | 63.0803 | 63.724 | 63.0803 | 61.7929 | 59.2182 | 57.2872 | 55.9998 | 57.9309 | 61.1493 | 63.724 | 64.3676 | 63.724 | 62.4366 | 57.9309 | 59.8619 | 4
5 | 29 | 69.488 | 69.488 | 67.872 | 67.064 | 67.872 | 67.872 | 70.296 | 72.72 | 76.76 | 79.184 | 79.992 | 79.184 | 77.568 | 74.336 | 71.912 | 70.296 | 72.72 | 76.76 | 79.992 | 80.8001 | 79.992 | 78.376 | 72.72 | 75.144 | 5
5 | 30 | 72.3649 | 72.3649 | 70.682 | 69.8406 | 70.682 | 70.682 | 73.2064 | 75.7307 | 79.938 | 82.4624 | 83.3038 | 82.4624 | 80.7795 | 77.4137 | 74.8893 | 73.2064 | 75.7307 | 79.938 | 83.3038 | 84.1453 | 83.3038 | 81.6209 | 75.7307 | 78.2551 | 5
5 | 31 | 70.5208 | 70.5208 | 68.8808 | 68.0607 | 68.8808 | 68.8808 | 71.3408 | 73.8008 | 77.9009 | 80.3609 | 81.1809 | 80.3609 | 78.7209 | 75.4408 | 72.9808 | 71.3408 | 73.8008 | 77.9009 | 81.1809 | 82.0009 | 81.1809 | 79.5409 | 73.8008 | 76.2608
5 | 32 | 73.7665 | 73.7665 | 72.051 | 71.1933 | 72.051 | 72.051 | 74.6243 | 77.1975 | 81.4862 | 84.0595 | 84.9172 | 84.0595 | 82.344 | 78.913 | 76.3397 | 74.6243 | 77.1975 | 81.4862 | 84.9172 | 85.775 | 84.9172 | 83.2018 | 77.1975 | 79.7708 | 5
5 | 33 | 71.9223 | 71.9223 | 70.2497 | 69.4134 | 70.2497 | 70.2497 | 72.7586 | 75.2676 | 79.4491 | 81.958 | 82.7943 | 81.958 | 80.2854 | 76.9402 | 74.4313 | 72.7586 | 75.2676 | 79.4491 | 82.7943 | 83.6306 | 82.7943 | 81.1217 | 75.2676 | 77.7765 | 5
5 | 34 | 51.7811 | 51.7811 | 50.5769 | 49.9748 | 50.5769 | 50.5769 | 52.3832 | 54.1896 | 57.2001 | 59.0064 | 59.6085 | 59.0064 | 57.8022 | 55.3938 | 53.5875 | 52.3832 | 54.1896 | 57.2001 | 59.6085 | 60.2106 | 59.6085 | 58.4043 | 54.1896 | 55.9959
5 | 35 | 50.1524 | 50.1524 | 48.986 | 48.4029 | 48.986 | 48.986 | 50.7355 | 52.485 | 55.4009 | 57.1504 | 57.7335 | 57.1504 | 55.984 | 53.6514 | 51.9019 | 50.7355 | 52.485 | 55.4009 | 57.7335 | 58.3167 | 57.7335 | 56.5672 | 52.485 | 54.2345 | 5
6 | 36 | 66.8215 | 63.5217 | 65.9965 | 65.1716 | 67.6464 | 69.2963 | 71.7712 | 74.2461 | 77.5459 | 78.3709 | 77.5459 | 76.721 | 75.071 | 72.5962 | 71.7712 | 75.071 | 78.3709 | 80.8457 | 82.4957 | 80.0208 | 77.5459 | 69.2963 | 72.5962 | 75.071 | 6
6 | 37 | 69.588 | 66.1515 | 68.7289 | 67.8697 | 70.4471 | 72.1653 | 74.7426 | 77.32 | 80.7564 | 81.6155 | 80.7564 | 79.8973 | 78.1791 | 75.6017 | 74.7426 | 78.1791 | 81.6155 | 84.1929 | 85.9111 | 83.3337 | 80.7564 | 72.1653 | 75.6017 | 78.1791
6 | 38 | 67.8146 | 64.4657 | 66.9774 | 66.1401 | 68.6518 | 70.3262 | 72.8379 | 75.3495 | 78.6984 | 79.5356 | 78.6984 | 77.8612 | 76.1867 | 73.6751 | 72.8379 | 76.1867 | 79.5356 | 82.0473 | 83.7217 | 81.21 | 78.6984 | 70.3262 | 73.6751 | 76.1867 | 6
6 | 39 | 70.9358 | 67.4328 | 70.06 | 69.1843 | 71.8115 | 73.563 | 76.1903 | 78.8175 | 82.3205 | 83.1963 | 82.3205 | 81.4448 | 79.6933 | 77.066 | 76.1903 | 79.6933 | 83.1963 | 85.8235 | 87.575 | 84.9478 | 82.3205 | 73.563 | 77.066 | 79.6933
6 | 40 | 69.1624 | 65.7469 | 68.3085 | 67.4546 | 70.0162 | 71.7239 | 74.2855 | 76.8471 | 80.2625 | 81.1163 | 80.2625 | 79.4086 | 77.7009 | 75.1394 | 74.2855 | 77.7009 | 81.1163 | 83.6779 | 85.3856 | 82.8241 | 80.2625 | 71.7239 | 75.1394 | 77.7009 | 6
6 | 41 | 51.4178 | 48.8786 | 50.783 | 50.1482 | 52.0526 | 53.3221 | 55.2265 | 57.1309 | 59.67 | 60.3048 | 59.67 | 59.0352 | 57.7657 | 55.8613 | 55.2265 | 57.7657 | 60.3048 | 62.2092 | 63.4787 | 61.5744 | 59.67 | 53.3221 | 55.8613 | 57.7657
6 | 42 | 49.8004 | 47.3412 | 49.1856 | 48.5708 | 50.4153 | 51.6449 | 53.4894 | 55.3338 | 57.7931 | 58.4079 | 57.7931 | 57.1783 | 55.9486 | 54.1042 | 53.4894 | 55.9486 | 58.4079 | 60.2524 | 61.482 | 59.6376 | 57.7931 | 51.6449 | 54.1042 | 55.9486 | 6
7 | 43 | 63.159 | 60.04 | 62.3792 | 61.5995 | 63.9387 | 65.4982 | 67.8374 | 70.1766 | 73.2956 | 74.0753 | 73.2956 | 72.5159 | 70.9564 | 68.6172 | 67.8374 | 70.9564 | 74.0753 | 76.4146 | 77.9741 | 75.6348 | 73.2956 | 65.4982 | 68.6172 | 70.9564 | 7
7 | 44 | 65.7738 | 62.5258 | 64.9618 | 64.1498 | 66.5859 | 68.2099 | 70.646 | 73.082 | 76.3301 | 77.1422 | 76.3301 | 75.5181 | 73.8941 | 71.458 | 70.646 | 73.8941 | 77.1422 | 79.5782 | 81.2023 | 78.7662 | 76.3301 | 68.2099 | 71.458 | 73.8941
7 | 45 | 64.0976 | 60.9323 | 63.3063 | 62.515 | 64.889 | 66.4716 | 68.8456 | 71.2196 | 74.3849 | 75.1763 | 74.3849 | 73.5936 | 72.0109 | 69.637 | 68.8456 | 72.0109 | 75.1763 | 77.5502 | 79.1329 | 76.7589 | 74.3849 | 66.4716 | 69.637 | 72.0109 | 7
7 | 46 | 67.0477 | 63.7368 | 66.22 | 65.3923 | 67.8755 | 69.531 | 72.0143 | 74.4975 | 77.8085 | 78.6363 | 77.8085 | 76.9808 | 75.3252 | 72.842 | 72.0143 | 75.3252 | 78.6363 | 81.1195 | 82.775 | 80.2917 | 77.8085 | 69.531 | 72.842 | 75.3252
7 | 47 | 65.3716 | 62.1433 | 64.5645 | 63.7574 | 66.1786 | 67.7927 | 70.2139 | 72.6351 | 75.8633 | 76.6703 | 75.8633 | 75.0562 | 73.4421 | 71.021 | 70.2139 | 73.4421 | 76.6703 | 79.0915 | 80.7056 | 78.2845 | 75.8633 | 67.7927 | 71.021 | 73.4421 | 7
7 | 48 | 48.5996 | 46.1996 | 47.9996 | 47.3996 | 49.1996 | 50.3995 | 52.1995 | 53.9995 | 56.3995 | 56.9995 | 56.3995 | 55.7995 | 54.5995 | 52.7995 | 52.1995 | 54.5995 | 56.9995 | 58.7995 | 59.9995 | 58.1995 | 56.3995 | 50.3995 | 52.7995 | 54.5995
7 | 49 | 47.0709 | 44.7464 | 46.4898 | 45.9086 | 47.652 | 48.8142 | 50.5576 | 52.301 | 54.6255 | 55.2066 | 54.6255 | 54.0443 | 52.8821 | 51.1387 | 50.5576 | 52.8821 | 55.2066 | 56.9499 | 58.1122 | 56.3688 | 54.6255 | 48.8142 | 51.1387 | 52.8821 | 7
8 | 50 | 57.6538 | 54.8067 | 56.942 | 56.2302 | 58.3656 | 59.7891 | 61.9244 | 64.0598 | 66.9069 | 67.6186 | 66.9069 | 66.1951 | 64.7715 | 62.6362 | 61.9244 | 64.7715 | 67.6186 | 69.754 | 71.1775 | 69.0422 | 66.9069 | 59.7891 | 62.6362 | 64.7715 | 8
8 | 51 | 60.0407 | 57.0758 | 59.2995 | 58.5582 | 60.782 | 62.2645 | 64.4882 | 66.7119 | 69.6769 | 70.4181 | 69.6769 | 68.9357 | 67.4532 | 65.2294 | 64.4882 | 67.4532 | 70.4181 | 72.6419 | 74.1244 | 71.9006 | 69.6769 | 62.2645 | 65.2294 | 67.4532 | 8
8 | 52 | 58.5106 | 55.6212 | 57.7883 | 57.0659 | 59.233 | 60.6777 | 62.8448 | 65.0118 | 67.9012 | 68.6236 | 67.9012 | 67.1789 | 65.7342 | 63.5671 | 62.8448 | 65.7342 | 68.6236 | 70.7907 | 72.2354 | 70.0683 | 67.9012 | 60.6777 | 63.5671 | 65.7342
8 | 53 | 61.2036 | 58.1812 | 60.448 | 59.6924 | 61.9592 | 63.4704 | 65.7372 | 68.004 | 71.0264 | 71.782 | 71.0264 | 70.2708 | 68.7596 | 66.4928 | 65.7372 | 68.7596 | 71.782 | 74.0488 | 75.56 | 73.2932 | 71.0264 | 63.4704 | 66.4928 | 68.7596 | 8
8 | 54 | 59.6735 | 56.7267 | 58.9368 | 58.2001 | 60.4102 | 61.8836 | 64.0938 | 66.3039 | 69.2507 | 69.9874 | 69.2507 | 68.514 | 67.0406 | 64.8305 | 64.0938 | 67.0406 | 69.9874 | 72.1976 | 73.671 | 71.4609 | 69.2507 | 61.8836 | 64.8305 | 67.0406
8 | 55 | 44.3634 | 42.1726 | 43.8157 | 43.268 | 44.9111 | 46.0065 | 47.6496 | 49.2927 | 51.4835 | 52.0312 | 51.4835 | 50.9358 | 49.8404 | 48.1973 | 47.6496 | 49.8404 | 52.0312 | 53.6743 | 54.7697 | 53.1266 | 51.4835 | 46.0065 | 48.1973 | 49.8404 | 8
8 | 56 | 42.968 | 40.8461 | 42.4375 | 41.907 | 43.4985 | 44.5594 | 46.1508 | 47.7422 | 49.8641 | 50.3946 | 49.8641 | 49.3336 | 48.2727 | 46.6813 | 46.1508 | 48.2727 | 50.3946 | 51.986 | 53.0469 | 51.4555 | 49.8641 | 44.5594 | 46.6813 | 48.2727 | 8
9 | 57 | 61.4335 | 62.2014 | 62.9693 | 64.5051 | 66.041 | 66.041 | 68.3447 | 69.1127 | 70.6485 | 72.1843 | 73.7202 | 72.9522 | 72.1843 | 70.6485 | 69.1127 | 69.1127 | 70.6485 | 76.7918 | 76.7918 | 76.7918 | 74.4881 | 71.4164 | 63.7372 | 63.7372 | 9
9 | 58 | 63.9769 | 64.7766 | 65.5763 | 67.1757 | 68.7752 | 68.7752 | 71.1743 | 71.974 | 73.5734 | 75.1729 | 76.7723 | 75.9726 | 75.1729 | 73.5734 | 71.974 | 71.974 | 73.5734 | 79.9711 | 79.9711 | 79.9711 | 77.572 | 74.3731 | 66.376 | 66.376
9 | 59 | 62.3465 | 63.1258 | 63.9052 | 65.4638 | 67.0225 | 67.0225 | 69.3605 | 70.1398 | 71.6985 | 73.2571 | 74.8158 | 74.0365 | 73.2571 | 71.6985 | 70.1398 | 70.1398 | 71.6985 | 77.9331 | 77.9331 | 77.9331 | 75.5951 | 72.4778 | 64.6845 | 64.6845 | 9
9 | 60 | 65.216 | 66.0312 | 66.8464 | 68.4768 | 70.1072 | 70.1072 | 72.5528 | 73.368 | 74.9984 | 76.6288 | 78.2592 | 77.444 | 76.6288 | 74.9984 | 73.368 | 73.368 | 74.9984 | 81.52 | 81.52 | 81.52 | 79.0744 | 75.8136 | 67.6616 | 67.6616
9 | 61 | 63.5856 | 64.3804 | 65.1752 | 66.7649 | 68.3545 | 68.3545 | 70.739 | 71.5338 | 73.1234 | 74.7131 | 76.3027 | 75.5079 | 74.7131 | 73.1234 | 71.5338 | 71.5338 | 73.1234 | 79.482 | 79.482 | 79.482 | 77.0975 | 73.9183 | 65.9701 | 65.9701 | 9
9 | 62 | 43.7886 | 44.336 | 44.8833 | 45.9781 | 47.0728 | 47.0728 | 48.7149 | 49.2622 | 50.3569 | 51.4516 | 52.5464 | 51.999 | 51.4516 | 50.3569 | 49.2622 | 49.2622 | 50.3569 | 54.7358 | 54.7358 | 54.7358 | 53.0937 | 50.9043 | 45.4307 | 45.4307
9 | 63 | 42.4113 | 42.9414 | 43.4716 | 44.5318 | 45.5921 | 45.5921 | 47.1825 | 47.7127 | 48.773 | 49.8332 | 50.8935 | 50.3634 | 49.8332 | 48.773 | 47.7127 | 47.7127 | 48.773 | 53.0141 | 53.0141 | 53.0141 | 51.4237 | 49.3031 | 44.0017 | 44.0017 | 9
10 | 64 | 66.0154 | 66.8406 | 67.6657 | 69.3161 | 70.9665 | 70.9665 | 73.4421 | 74.2673 | 75.9177 | 77.568 | 79.2184 | 78.3932 | 77.568 | 75.9177 | 74.2673 | 74.2673 | 75.9177 | 82.5192 | 82.5192 | 82.5192 | 80.0436 | 76.7429 | 68.4909 | 68.4909 | 10
10 | 65 | 68.7485 | 69.6078 | 70.4672 | 72.1859 | 73.9046 | 73.9046 | 76.4827 | 77.342 | 79.0608 | 80.7795 | 82.4982 | 81.6388 | 80.7795 | 79.0608 | 77.342 | 77.342 | 79.0608 | 85.9356 | 85.9356 | 85.9356 | 83.3575 | 79.9201 | 71.3265 | 71.3265
10 | 66 | 66.9965 | 67.8339 | 68.6714 | 70.3463 | 72.0212 | 72.0212 | 74.5336 | 75.371 | 77.046 | 78.7209 | 80.3958 | 79.5583 | 78.7209 | 77.046 | 75.371 | 75.371 | 77.046 | 83.7456 | 83.7456 | 83.7456 | 81.2332 | 77.8834 | 69.5088 | 69.5088 | 10
10 | 67 | 70.08 | 70.956 | 71.832 | 73.584 | 75.336 | 75.336 | 77.964 | 78.84 | 80.592 | 82.344 | 84.096 | 83.22 | 82.344 | 80.592 | 78.84 | 78.84 | 80.592 | 87.6 | 87.6 | 87.6 | 84.972 | 81.468 | 72.708 | 72.708 | 10
10 | 68 | 68.328 | 69.1821 | 70.0362 | 71.7444 | 73.4526 | 73.4526 | 76.0149 | 76.869 | 78.5772 | 80.2854 | 81.9936 | 81.1395 | 80.2854 | 78.5772 | 76.869 | 76.869 | 78.5772 | 85.41 | 85.41 | 85.41 | 82.8477 | 79.4313 | 70.8903 | 70.8903
10 | 69 | 47.0545 | 47.6427 | 48.2309 | 49.4072 | 50.5836 | 50.5836 | 52.3481 | 52.9363 | 54.1127 | 55.2891 | 56.4654 | 55.8772 | 55.2891 | 54.1127 | 52.9363 | 52.9363 | 54.1127 | 58.8181 | 58.8181 | 58.8181 | 57.0536 | 54.7009 | 48.8191 | 48.8191 | 10
10 | 70 | 45.5744 | 46.1441 | 46.7138 | 47.8531 | 48.9925 | 48.9925 | 50.7015 | 51.2712 | 52.4106 | 53.55 | 54.6893 | 54.1196 | 53.55 | 52.4106 | 51.2712 | 51.2712 | 52.4106 | 56.968 | 56.968 | 56.968 | 55.259 | 52.9803 | 47.2835 | 47.2835 | 10
11 | 71 | 67.1156 | 67.9546 | 68.7935 | 70.4714 | 72.1493 | 72.1493 | 74.6661 | 75.5051 | 77.183 | 78.8608 | 80.5387 | 79.6998 | 78.8608 | 77.183 | 75.5051 | 75.5051 | 77.183 | 83.8945 | 83.8945 | 83.8945 | 81.3777 | 78.0219 | 69.6325 | 69.6325 | 11
11 | 72 | 69.8943 | 70.768 | 71.6416 | 73.389 | 75.1364 | 75.1364 | 77.7574 | 78.6311 | 80.3784 | 82.1258 | 83.8731 | 82.9995 | 82.1258 | 80.3784 | 78.6311 | 78.6311 | 80.3784 | 87.3679 | 87.3679 | 87.3679 | 84.7468 | 81.2521 | 72.5153 | 72.5153
11 | 73 | 68.1131 | 68.9645 | 69.8159 | 71.5187 | 73.2216 | 73.2216 | 75.7758 | 76.6272 | 78.3301 | 80.0329 | 81.7357 | 80.8843 | 80.0329 | 78.3301 | 76.6272 | 76.6272 | 78.3301 | 85.1414 | 85.1414 | 85.1414 | 82.5871 | 79.1815 | 70.6673 | 70.6673 | 11
11 | 74 | 71.248 | 72.1386 | 73.0292 | 74.8104 | 76.5916 | 76.5916 | 79.2634 | 80.154 | 81.9352 | 83.7164 | 85.4976 | 84.607 | 83.7164 | 81.9352 | 80.154 | 80.154 | 81.9352 | 89.06 | 89.06 | 89.06 | 86.3882 | 82.8258 | 73.9198 | 73.9198
11 | 75 | 69.4668 | 70.3351 | 71.2035 | 72.9401 | 74.6768 | 74.6768 | 77.2818 | 78.1501 | 79.8868 | 81.6235 | 83.3602 | 82.4918 | 81.6235 | 79.8868 | 78.1501 | 78.1501 | 79.8868 | 86.8335 | 86.8335 | 86.8335 | 84.2285 | 80.7552 | 72.0718 | 72.0718 | 11
11 | 76 | 47.8388 | 48.4367 | 49.0347 | 50.2307 | 51.4267 | 51.4267 | 53.2206 | 53.8186 | 55.0146 | 56.2105 | 57.4065 | 56.8085 | 56.2105 | 55.0146 | 53.8186 | 53.8186 | 55.0146 | 59.7984 | 59.7984 | 59.7984 | 58.0045 | 55.6126 | 49.6327 | 49.6327
11 | 77 | 46.334 | 46.9132 | 47.4923 | 48.6507 | 49.809 | 49.809 | 51.5466 | 52.1257 | 53.2841 | 54.4424 | 55.6008 | 55.0216 | 54.4424 | 53.2841 | 52.1257 | 52.1257 | 53.2841 | 57.9175 | 57.9175 | 57.9175 | 56.18 | 53.8633 | 48.0715 | 48.0715 | 11
12 | 78 | 68.9167 | 64.6094 | 67.1938 | 68.9167 | 71.5011 | 74.0855 | 76.6699 | 77.5313 | 79.2542 | 81.8386 | 80.9771 | 82.7001 | 82.7001 | 80.9771 | 77.5313 | 77.5313 | 80.1157 | 82.7001 | 86.1459 | 86.1459 | 85.2844 | 80.9771 | 72.3626 | 71.5011 | 12
12 | 79 | 71.77 | 67.2843 | 69.9757 | 71.77 | 74.4613 | 77.1527 | 79.8441 | 80.7412 | 82.5355 | 85.2268 | 84.3297 | 86.124 | 86.124 | 84.3297 | 80.7412 | 80.7412 | 83.4326 | 86.124 | 89.7124 | 89.7124 | 88.8153 | 84.3297 | 75.3585 | 74.4613
12 | 80 | 69.941 | 65.5696 | 68.1924 | 69.941 | 72.5637 | 75.1865 | 77.8093 | 78.6836 | 80.4321 | 83.0549 | 82.1806 | 83.9292 | 83.9292 | 82.1806 | 78.6836 | 78.6836 | 81.3064 | 83.9292 | 87.4262 | 87.4262 | 86.5519 | 82.1806 | 73.438 | 72.5637
12 | 81 | 73.16 | 68.5875 | 71.331 | 73.16 | 75.9035 | 78.647 | 81.3905 | 82.305 | 84.134 | 86.8775 | 85.963 | 87.792 | 87.792 | 85.963 | 82.305 | 82.305 | 85.0485 | 87.792 | 91.45 | 91.45 | 90.5355 | 85.963 | 76.818 | 75.9035 | 12
12 | 82 | 71.331 | 66.8728 | 69.5477 | 71.331 | 74.0059 | 76.6808 | 79.3557 | 80.2474 | 82.0306 | 84.7056 | 83.8139 | 85.5972 | 85.5972 | 83.8139 | 80.2474 | 80.2474 | 82.9223 | 85.5972 | 89.1637 | 89.1637 | 88.2721 | 83.8139 | 74.8975 | 74.0059 | 12
12 | 83 | 50.239 | 47.099 | 48.983 | 50.239 | 52.1229 | 54.0069 | 55.8909 | 56.5188 | 57.7748 | 59.6588 | 59.0308 | 60.2868 | 60.2868 | 59.0308 | 56.5188 | 56.5188 | 58.4028 | 60.2868 | 62.7987 | 62.7987 | 62.1707 | 59.0308 | 52.7509 | 52.1229
12 | 84 | 48.6587 | 45.6175 | 47.4422 | 48.6587 | 50.4834 | 52.3081 | 54.1328 | 54.7411 | 55.9575 | 57.7822 | 57.174 | 58.3905 | 58.3905 | 57.174 | 54.7411 | 54.7411 | 56.5658 | 58.3905 | 60.8234 | 60.8234 | 60.2152 | 57.174 | 51.0917 | 50.4834 | 12

## Traditional Generators
[8 empty] | Fuel |  | Ramping Rate [MW/sec] |  | Inertia |  | Governor | [7 empty] | Excitation Type and Data | [10 empty] | Lifetime Year
Bus ID | Type | Size [MVA] | Pmin | Qmin | Qmax | R/X | rpm | Type | Consumption [ton/MW] | Up | Down | Ta [s] | Kg*m2 | R | Pmax | t1 | t2 | t3 | t4 | t5 | F | tR | tA1 | tA2 | tE | tF | kA | kE | kF | sE | Vmax [pu] | Vmin [pu] | From | To
3 | DG | 6 | 1 | -2 | 2 | 0.07 | 1000 | Diesel | 0.249 | 0.03 | 0.03 | 0.28622 | 156.6 | 0.07 | 4.905 | 0.23 | 0.0001 | 0.305 | 0.09 | 0.0001 | 1.03 | 0.0001 | 20 | 0.0001 | 0.7 | 0.0001 | 0.05 | 1 | 0.0001 | 0.414 | 6.812 | 1.095 | 2008 | 2028
7 | DG | 14 | 1 | -4 | 4 | 0.07 | 1000 | Diesel | 0.237 | 0.03 | 0.03 | 0.10966 | 140 | 0.05 | 13 | 0.2 | 0.0001 | 0.3 | 0.09 | 0.0001 | 1 | 0.0001 | 20.1 | 0.0001 | 0.7 | 0.0001 | 0.05 | 1 | 0.0001 | 0.414 | 7.1 | 1.4 | 2001 | 2023
8 | DG | 18.5 | 3 | -6 | 6 | 0.07 | 750 | Heavy Oil 380 | 0.186 | 0.04 | 0.04 | 1.7489 | 5245 | 0.05 | 16.5 | 0.19 | 0.0001 | 0.28 | 0.08 | 0.0001 | 1 | 0.0001 | 20.15 | 0.0001 | 0.76 | 0.0001 | 0.05 | 1 | 0.0001 | 0.95 | 5.94 | 1.21 | 2013 | 2033
9 | DG | 28 | 8 | -7 | 7 | 0.07 | 500 | Diesel | 0.186 | 0.04 | 0.04 | 0.79799 | 8150 | 0.05 | 20.7 | 0.2 | 0.0001 | 0.3 | 0.09 | 0.0001 | 1.01 | 0.0001 | 20 | 0.0001 | 1.97 | 0.0001 | 0.05 | 1 | 0.0001 | 0.375 | 4.39 | 0.0001 | 2010 | 2030
10 | DG | 28 | 8 | -7 | 7 | 0.07 | 500 | Diesel | 0.186 | 0.04 | 0.04 | 0.79799 | 8150 | 0.05 | 20.7 | 0.2 | 0.0001 | 0.3 | 0.09 | 0.0001 | 1.01 | 0.0001 | 20 | 0.0001 | 1.97 | 0.0001 | 0.05 | 1 | 0.0001 | 0.375 | 4.39 | 0.0001 | 2010 | 2030
96 | DG | 3.2 | 1 | -1.5 | 1.5 | 0.15 | 1500 | Diesel | 0.22 | 0.04 | 0.04 | 1.0795 | 140 | 0.06 | 3.4 | 0.19 | 0.0001 | 0.3 | 0.08 | 0.0001 | 1 | 0.0001 | 20 | 0.0001 | 0.099 | 0.0001 | 0.05 | 1 | 0.0001 | 0.355 | 4 | 0.001 | 2009 | 2029
97 | DG | 1 | 0.4 | -0.4 | 0.4 | 0.15 | 1000 | Diesel | 0.24 | 0.04 | 0.04 | 1.0966 | 100 | 0.07 | 0.9 | 0.18 | 0.0001 | 0.3 | 0.08 | 0.0001 | 1.01 | 0.0001 | 20 | 0.0001 | 0.89 | 0.0001 | 0.05 | 1 | 0.0001 | 0.325 | 3.8 | 0.001 | 2009 | 2029
9870
Governor and Excitation models as from Appendix D -> Anderson, P. M., & Fouad, A. A. (2008). Power system control and stability. John Wiley & Sons.
D.13 |  | D.4

## Renewable Generators
Bus ID | Type | Size [MVA] | Qmin | Qmax | Existing
1 | PV | 4.4 | -4.4 | 4.4 | 1
59 | WS | 9.35 | -9.35 | 9.35 | 1
3 | WS | 5 | -5 | 5 | 0
7 | PV | 14 | -14 | 14 | 0
8 | PV | 20 | -20 | 20 | 0
9 | PV | 25 | -25 | 25 | 0
10 | PV | 25 | -25 | 25 | 0
96 | WW | 5 | -5 | 5 | 0
97 | PV | 1 | -1 | 1 | 0
56 | WS | 30 | -30 | 30 | 0
12 | WW | 50 | -50 | 50 | 0
77 | WE | 20 | -20 | 20 | 0
74 | WN | 15 | -15 | 15 | 0
76 | PV | 10 | -10 | 10 | 0

## Hourly Solar Profile
Example of one location there will be another document explaining how I got this data from global solar atlas
Hours
Month | Week | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6831 | 32.7688 | 45.9194 | 55.5129 | 61.8727 | 63.1662 | 60.7947 | 56.0519 | 48.8298 | 36.9727 | 17.6779 | 0.10779 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7613 | 33.1521 | 46.4565 | 56.1622 | 62.5963 | 63.9049 | 61.5058 | 56.7075 | 49.4009 | 37.4051 | 17.8847 | 0.10905 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8394 | 33.5353 | 46.9936 | 56.8115 | 63.32 | 64.6437 | 62.2168 | 57.363 | 49.972 | 37.8375 | 18.0914 | 0.11031 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8639 | 33.6551 | 47.1614 | 57.0144 | 63.5461 | 64.8746 | 62.439 | 57.5679 | 50.1505 | 37.9727 | 18.156 | 0.11071 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8883 | 33.7749 | 47.3292 | 57.2173 | 63.7722 | 65.1055 | 62.6612 | 57.7728 | 50.329 | 38.1078 | 18.2206 | 0.1111 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5921 | 36.1245 | 52.0684 | 62.9949 | 69.6847 | 71.4686 | 70.1306 | 65.7823 | 55.7477 | 43.1487 | 24.529 | 1.6724 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6295 | 36.2522 | 52.2524 | 63.2175 | 69.9309 | 71.7211 | 70.3785 | 66.0148 | 55.9447 | 43.3012 | 24.6157 | 1.6783 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3219 | 38.6137 | 55.6561 | 67.3356 | 74.4863 | 76.3931 | 74.963 | 70.315 | 59.589 | 46.1219 | 26.2192 | 1.7877 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 21.2464 | 48.8161 | 67.2802 | 80.4327 | 88.4001 | 89.6648 | 87.7678 | 82.4562 | 71.7066 | 55.8982 | 32.7548 | 2.7823 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4709 | 51.6295 | 71.1577 | 85.0683 | 93.4949 | 94.8324 | 92.8261 | 87.2084 | 75.8392 | 59.1198 | 34.6426 | 2.9426 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 23.6953 | 54.4429 | 75.0353 | 89.7038 | 98.5896 | 100 | 97.8843 | 91.9605 | 79.9718 | 62.3413 | 36.5303 | 3.103 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 23.6292 | 54.2908 | 74.8257 | 89.4532 | 98.3142 | 99.7207 | 97.6109 | 91.7036 | 79.7484 | 62.1672 | 36.4283 | 3.0943 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 23.563 | 54.1387 | 74.6161 | 89.2027 | 98.0388 | 99.4413 | 97.3375 | 91.4468 | 79.525 | 61.9931 | 36.3262 | 3.0856 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 0 | 0 | 0 | 0 | 0 | 1.3986 | 31.329 | 57.9028 | 76.7841 | 90.7703 | 97.7634 | 99.0221 | 97.2039 | 91.05 | 78.6023 | 60.2804 | 36.9235 | 5.3147 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 0 | 0 | 0 | 0 | 0 | 1.3947 | 31.2408 | 57.7397 | 76.5678 | 90.5146 | 97.488 | 98.7432 | 96.9301 | 90.7935 | 78.3809 | 60.1106 | 36.8195 | 5.2998 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 0 | 0 | 0 | 0 | 0 | 1.3947 | 31.2408 | 57.7397 | 76.5678 | 90.5146 | 97.488 | 98.7432 | 96.9301 | 90.7935 | 78.3809 | 60.1106 | 36.8195 | 5.2998 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 0 | 0 | 0 | 0 | 0 | 1.3947 | 31.2408 | 57.7397 | 76.5678 | 90.5146 | 97.488 | 98.7432 | 96.9301 | 90.7935 | 78.3809 | 60.1106 | 36.8195 | 5.2998 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 0 | 0 | 0 | 0 | 0 | 5.2998 | 36.4011 | 56.6239 | 74.3363 | 87.4463 | 92.8856 | 93.7224 | 92.1882 | 86.0516 | 73.9179 | 56.345 | 35.1459 | 5.0208 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 0 | 0 | 0 | 0 | 0 | 5.2998 | 36.4011 | 56.6239 | 74.3363 | 87.4463 | 92.8856 | 93.7224 | 92.1882 | 86.0516 | 73.9179 | 56.345 | 35.1459 | 5.0208 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 0 | 0 | 0 | 0 | 0 | 5.2998 | 36.4011 | 56.6239 | 74.3363 | 87.4463 | 92.8856 | 93.7224 | 92.1882 | 86.0516 | 73.9179 | 56.345 | 35.1459 | 5.0208 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 0 | 0 | 0 | 0 | 0 | 4.9854 | 34.2417 | 53.2649 | 69.9266 | 82.2588 | 87.3754 | 88.1626 | 86.7194 | 80.9469 | 69.533 | 53.0025 | 33.061 | 4.723 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 0 | 0 | 0 | 0 | 0 | 4.671 | 32.0823 | 49.9058 | 65.5168 | 77.0713 | 81.8652 | 82.6028 | 81.2506 | 75.8421 | 65.148 | 49.66 | 30.976 | 4.4251 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 0 | 0 | 0 | 0 | 0 | 2.5222 | 18.8022 | 32.9038 | 46.0882 | 56.7504 | 62.8267 | 64.5464 | 63.7439 | 59.0433 | 48.4958 | 35.426 | 20.2926 | 2.9808 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 0 | 0 | 0 | 0 | 0 | 2.3402 | 17.4453 | 30.5293 | 42.7623 | 52.655 | 58.2928 | 59.8884 | 59.1438 | 54.7825 | 44.9961 | 32.8695 | 18.8282 | 2.7657 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 0 | 0 | 0 | 0 | 0 | 2.1842 | 16.2823 | 28.494 | 39.9114 | 49.1447 | 54.4066 | 55.8959 | 55.2009 | 51.1303 | 41.9964 | 30.6782 | 17.5729 | 2.5813 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 0 | 0 | 0 | 0 | 0 | 2.0282 | 15.1193 | 26.4587 | 37.0606 | 45.6343 | 50.5204 | 51.9033 | 51.258 | 47.4782 | 38.9966 | 28.4869 | 16.3177 | 2.397 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 0 | 0 | 0 | 0 | 0 | 0.85099 | 9.5311 | 17.2751 | 23.9979 | 30.2101 | 33.9545 | 34.5502 | 34.0396 | 31.1462 | 25.6148 | 17.7857 | 10.5523 | 1.5318 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 0 | 0 | 0 | 0 | 0 | 0.78007 | 8.7368 | 15.8355 | 21.9981 | 27.6926 | 31.125 | 31.671 | 31.203 | 28.5507 | 23.4802 | 16.3036 | 9.6729 | 1.4041 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 0 | 0 | 0 | 0 | 0 | 0.76432 | 8.5603 | 15.5156 | 21.5537 | 27.1332 | 30.4962 | 31.0312 | 30.5726 | 27.9739 | 23.0059 | 15.9742 | 9.4775 | 1.3758 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 0 | 0 | 0 | 0 | 0 | 0.74856 | 8.3838 | 15.1957 | 21.1093 | 26.5737 | 29.8674 | 30.3914 | 29.9422 | 27.3972 | 22.5315 | 15.6448 | 9.2821 | 1.3474 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 0 | 0 | 0 | 0 | 0 | 0.21984 | 8.4272 | 15.6086 | 19.7855 | 23.6693 | 25.5013 | 25.3548 | 24.9884 | 23.3029 | 19.126 | 13.7766 | 8.7203 | 1.2458 | 0 | 0 | 0 | 0 | 0 | 0
8 | 32 | 0 | 0 | 0 | 0 | 0 | 0.21511 | 8.2459 | 15.2729 | 19.36 | 23.1603 | 24.9529 | 24.8095 | 24.451 | 22.8018 | 18.7147 | 13.4803 | 8.5328 | 1.219 | 0 | 0 | 0 | 0 | 0 | 0
8 | 33 | 0 | 0 | 0 | 0 | 0 | 0.21038 | 8.0647 | 14.9372 | 18.9345 | 22.6513 | 24.4045 | 24.2642 | 23.9136 | 22.3007 | 18.3034 | 13.184 | 8.3452 | 1.1922 | 0 | 0 | 0 | 0 | 0 | 0
8 | 34 | 0 | 0 | 0 | 0 | 0 | 0.21984 | 8.4272 | 15.6086 | 19.7855 | 23.6693 | 25.5013 | 25.3548 | 24.9884 | 23.3029 | 19.126 | 13.7766 | 8.7203 | 1.2458 | 0 | 0 | 0 | 0 | 0 | 0
8 | 35 | 0 | 0 | 0 | 0 | 0 | 0.22929 | 8.7896 | 16.2799 | 20.6365 | 24.6874 | 26.5982 | 26.4453 | 26.0631 | 24.3052 | 19.9486 | 14.3691 | 9.0954 | 1.2993 | 0 | 0 | 0 | 0 | 0 | 0
9 | 36 | 0 | 0 | 0 | 0 | 0 | 0.31833 | 11.3804 | 20.6917 | 27.9337 | 34.0617 | 35.4942 | 34.3004 | 33.1067 | 30.4804 | 24.7504 | 17.8267 | 8.7542 | 0.31833 | 0 | 0 | 0 | 0 | 0 | 0
9 | 37 | 0 | 0 | 0 | 0 | 0 | 0.33094 | 11.8311 | 21.5111 | 29.04 | 35.4106 | 36.8999 | 35.6588 | 34.4178 | 31.6876 | 25.7306 | 18.5327 | 9.1009 | 0.33094 | 0 | 0 | 0 | 0 | 0 | 0
9 | 38 | 0 | 0 | 0 | 0 | 0 | 0.3467 | 12.3945 | 22.5355 | 30.4229 | 37.0969 | 38.657 | 37.3569 | 36.0568 | 33.1965 | 26.9559 | 19.4152 | 9.5342 | 0.3467 | 0 | 0 | 0 | 0 | 0 | 0
9 | 39 | 0 | 0 | 0 | 0 | 0 | 0.36246 | 12.9579 | 23.5598 | 31.8058 | 38.7831 | 40.4141 | 39.0549 | 37.6957 | 34.7054 | 28.1812 | 20.2977 | 9.9676 | 0.36246 | 0 | 0 | 0 | 0 | 0 | 0
10 | 40 | 0 | 0 | 0 | 0 | 0 | 0.47277 | 15.9797 | 30.352 | 41.4148 | 50.0193 | 51.9104 | 50.6812 | 47.3718 | 42.8332 | 35.3634 | 24.1114 | 7.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 41 | 0 | 0 | 0 | 0 | 0 | 0.49247 | 16.6455 | 31.6166 | 43.1405 | 52.1034 | 54.0733 | 52.7929 | 49.3456 | 44.6179 | 36.8368 | 25.116 | 7.3871 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 42 | 0 | 0 | 0 | 0 | 0 | 0.51217 | 17.3113 | 32.8813 | 44.8661 | 54.1876 | 56.2363 | 54.9046 | 51.3194 | 46.4026 | 38.3103 | 26.1207 | 7.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 43 | 0 | 0 | 0 | 0 | 0 | 0.51414 | 17.3779 | 33.0078 | 45.0386 | 54.396 | 56.4526 | 55.1158 | 51.5168 | 46.5811 | 38.4577 | 26.2211 | 7.7121 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 44 | 0 | 0 | 0 | 0 | 0 | 0.51611 | 17.4445 | 33.1342 | 45.2112 | 54.6044 | 56.6688 | 55.327 | 51.7142 | 46.7595 | 38.605 | 26.3216 | 7.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 45 | 0 | 0 | 0 | 0 | 0 | 0.10362 | 17.3039 | 35.0222 | 47.0416 | 56.0562 | 59.89 | 59.3719 | 55.849 | 49.9429 | 41.1355 | 28.2871 | 5.9061 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 46 | 0 | 0 | 0 | 0 | 0 | 0.10401 | 17.3697 | 35.1553 | 47.2205 | 56.2694 | 60.1177 | 59.5977 | 56.0613 | 50.1328 | 41.2919 | 28.3947 | 5.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 47 | 0 | 0 | 0 | 0 | 0 | 0.10401 | 17.3697 | 35.1553 | 47.2205 | 56.2694 | 60.1177 | 59.5977 | 56.0613 | 50.1328 | 41.2919 | 28.3947 | 5.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 48 | 0 | 0 | 0 | 0 | 0 | 0.10401 | 17.3697 | 35.1553 | 47.2205 | 56.2694 | 60.1177 | 59.5977 | 56.0613 | 50.1328 | 41.2919 | 28.3947 | 5.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9048 | 32.6591 | 45.3483 | 53.5651 | 57.3095 | 57.7255 | 55.4373 | 50.0288 | 42.124 | 30.9949 | 9.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9048 | 32.6591 | 45.3483 | 53.5651 | 57.3095 | 57.7255 | 55.4373 | 50.0288 | 42.124 | 30.9949 | 9.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0006 | 33.055 | 45.898 | 54.2144 | 58.0041 | 58.4252 | 56.1092 | 50.6352 | 42.6346 | 31.3706 | 9.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0964 | 33.4508 | 46.4477 | 54.8636 | 58.6988 | 59.1249 | 56.7812 | 51.2416 | 43.1452 | 31.7463 | 9.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Equivalent Week Profile Solar
Month | Day | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Original
1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6831 | 32.7688 | 45.9194 | 55.5129 | 61.8727 | 63.1662 | 60.7947 | 56.0519 | 48.8298 | 36.9727 | 17.6779 | 0.10779 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7613 | 33.1521 | 46.4565 | 56.1622 | 62.5963 | 63.9049 | 61.5058 | 56.7075 | 49.4009 | 37.4051 | 17.8847 | 0.10905 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8072 | 33.3772 | 46.772 | 56.5436 | 63.0215 | 64.339 | 61.9235 | 57.0926 | 49.7364 | 37.6592 | 18.0061 | 0.10979 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8394 | 33.5353 | 46.9936 | 56.8115 | 63.32 | 64.6437 | 62.2168 | 57.363 | 49.972 | 37.8375 | 18.0914 | 0.11031 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8072 | 33.3772 | 46.772 | 56.5436 | 63.0215 | 64.339 | 61.9235 | 57.0926 | 49.7364 | 37.6592 | 18.0061 | 0.10979 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8639 | 33.6551 | 47.1614 | 57.0144 | 63.5461 | 64.8746 | 62.439 | 57.5679 | 50.1505 | 37.9727 | 18.156 | 0.11071 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8883 | 33.7749 | 47.3292 | 57.2173 | 63.7722 | 65.1055 | 62.6612 | 57.7728 | 50.329 | 38.1078 | 18.2206 | 0.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8478 | 36.9968 | 53.3256 | 64.516 | 71.3673 | 73.1943 | 71.824 | 67.3707 | 57.0938 | 44.1906 | 25.1213 | 1.7128 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5921 | 36.1245 | 52.0684 | 62.9949 | 69.6847 | 71.4686 | 70.1306 | 65.7823 | 55.7477 | 43.1487 | 24.529 | 1.6724 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8478 | 36.9968 | 53.3256 | 64.516 | 71.3673 | 73.1943 | 71.824 | 67.3707 | 57.0938 | 44.1906 | 25.1213 | 1.7128 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6295 | 36.2522 | 52.2524 | 63.2175 | 69.9309 | 71.7211 | 70.3785 | 66.0148 | 55.9447 | 43.3012 | 24.6157 | 1.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8478 | 36.9968 | 53.3256 | 64.516 | 71.3673 | 73.1943 | 71.824 | 67.3707 | 57.0938 | 44.1906 | 25.1213 | 1.7128 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3219 | 38.6137 | 55.6561 | 67.3356 | 74.4863 | 76.3931 | 74.963 | 70.315 | 59.589 | 46.1219 | 26.2192 | 1.7877 | 0 | 0 | 0 | 0 | 0 | 0 | 2
2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8478 | 36.9968 | 53.3256 | 64.516 | 71.3673 | 73.1943 | 71.824 | 67.3707 | 57.0938 | 44.1906 | 25.1213 | 1.7128 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 21.2464 | 48.8161 | 67.2802 | 80.4327 | 88.4001 | 89.6648 | 87.7678 | 82.4562 | 71.7066 | 55.8982 | 32.7548 | 2.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 3
3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4709 | 51.6295 | 71.1577 | 85.0683 | 93.4949 | 94.8324 | 92.8261 | 87.2084 | 75.8392 | 59.1198 | 34.6426 | 2.9426 | 0 | 0 | 0 | 0 | 0 | 0 | 3
3 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9209 | 52.6636 | 72.583 | 86.7721 | 95.3675 | 96.7318 | 94.6853 | 88.9551 | 77.3582 | 60.3039 | 35.3365 | 3.0016 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 23.6953 | 54.4429 | 75.0353 | 89.7038 | 98.5896 | 100 | 97.8843 | 91.9605 | 79.9718 | 62.3413 | 36.5303 | 3.103 | 0 | 0 | 0 | 0 | 0 | 0 | 3
3 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9209 | 52.6636 | 72.583 | 86.7721 | 95.3675 | 96.7318 | 94.6853 | 88.9551 | 77.3582 | 60.3039 | 35.3365 | 3.0016 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 23.6292 | 54.2908 | 74.8257 | 89.4532 | 98.3142 | 99.7207 | 97.6109 | 91.7036 | 79.7484 | 62.1672 | 36.4283 | 3.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 3
3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 23.563 | 54.1387 | 74.6161 | 89.2027 | 98.0388 | 99.4413 | 97.3375 | 91.4468 | 79.525 | 61.9931 | 36.3262 | 3.0856 | 0 | 0 | 0 | 0 | 0 | 0 | 3
4 | 22 | 0 | 0 | 0 | 0 | 0 | 1.3986 | 31.329 | 57.9028 | 76.7841 | 90.7703 | 97.7634 | 99.0221 | 97.2039 | 91.05 | 78.6023 | 60.2804 | 36.9235 | 5.3147 | 0 | 0 | 0 | 0 | 0 | 0 | 4
4 | 23 | 0 | 0 | 0 | 0 | 0 | 1.3957 | 31.2629 | 57.7805 | 76.6219 | 90.5785 | 97.5569 | 98.8129 | 96.9986 | 90.8577 | 78.4363 | 60.1531 | 36.8455 | 5.3035 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 0 | 0 | 0 | 0 | 0 | 1.3947 | 31.2408 | 57.7397 | 76.5678 | 90.5146 | 97.488 | 98.7432 | 96.9301 | 90.7935 | 78.3809 | 60.1106 | 36.8195 | 5.2998 | 0 | 0 | 0 | 0 | 0 | 0 | 4
4 | 25 | 0 | 0 | 0 | 0 | 0 | 1.3957 | 31.2629 | 57.7805 | 76.6219 | 90.5785 | 97.5569 | 98.8129 | 96.9986 | 90.8577 | 78.4363 | 60.1531 | 36.8455 | 5.3035 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 0 | 0 | 0 | 0 | 0 | 1.3947 | 31.2408 | 57.7397 | 76.5678 | 90.5146 | 97.488 | 98.7432 | 96.9301 | 90.7935 | 78.3809 | 60.1106 | 36.8195 | 5.2998 | 0 | 0 | 0 | 0 | 0 | 0 | 4
4 | 27 | 0 | 0 | 0 | 0 | 0 | 1.3957 | 31.2629 | 57.7805 | 76.6219 | 90.5785 | 97.5569 | 98.8129 | 96.9986 | 90.8577 | 78.4363 | 60.1531 | 36.8455 | 5.3035 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 0 | 0 | 0 | 0 | 0 | 1.3947 | 31.2408 | 57.7397 | 76.5678 | 90.5146 | 97.488 | 98.7432 | 96.9301 | 90.7935 | 78.3809 | 60.1106 | 36.8195 | 5.2998 | 0 | 0 | 0 | 0 | 0 | 0 | 4
5 | 29 | 0 | 0 | 0 | 0 | 0 | 5.2998 | 36.4011 | 56.6239 | 74.3363 | 87.4463 | 92.8856 | 93.7224 | 92.1882 | 86.0516 | 73.9179 | 56.345 | 35.1459 | 5.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 5
5 | 30 | 0 | 0 | 0 | 0 | 0 | 5.2998 | 36.4011 | 56.6239 | 74.3363 | 87.4463 | 92.8856 | 93.7224 | 92.1882 | 86.0516 | 73.9179 | 56.345 | 35.1459 | 5.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 5
5 | 31 | 0 | 0 | 0 | 0 | 0 | 5.1111 | 35.1055 | 54.6085 | 71.6905 | 84.3338 | 89.5795 | 90.3865 | 88.907 | 82.9888 | 71.287 | 54.3395 | 33.8949 | 4.8421 | 0 | 0 | 0 | 0 | 0 | 0
5 | 32 | 0 | 0 | 0 | 0 | 0 | 5.2998 | 36.4011 | 56.6239 | 74.3363 | 87.4463 | 92.8856 | 93.7224 | 92.1882 | 86.0516 | 73.9179 | 56.345 | 35.1459 | 5.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 5
5 | 33 | 0 | 0 | 0 | 0 | 0 | 4.9854 | 34.2417 | 53.2649 | 69.9266 | 82.2588 | 87.3754 | 88.1626 | 86.7194 | 80.9469 | 69.533 | 53.0025 | 33.061 | 4.723 | 0 | 0 | 0 | 0 | 0 | 0 | 5
5 | 34 | 0 | 0 | 0 | 0 | 0 | 5.1111 | 35.1055 | 54.6085 | 71.6905 | 84.3338 | 89.5795 | 90.3865 | 88.907 | 82.9888 | 71.287 | 54.3395 | 33.8949 | 4.8421 | 0 | 0 | 0 | 0 | 0 | 0
5 | 35 | 0 | 0 | 0 | 0 | 0 | 4.671 | 32.0823 | 49.9058 | 65.5168 | 77.0713 | 81.8652 | 82.6028 | 81.2506 | 75.8421 | 65.148 | 49.66 | 30.976 | 4.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 5
6 | 36 | 0 | 0 | 0 | 0 | 0 | 2.5222 | 18.8022 | 32.9038 | 46.0882 | 56.7504 | 62.8267 | 64.5464 | 63.7439 | 59.0433 | 48.4958 | 35.426 | 20.2926 | 2.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 6
6 | 37 | 0 | 0 | 0 | 0 | 0 | 2.2687 | 16.9122 | 29.5964 | 41.4556 | 51.0461 | 56.5116 | 58.0585 | 57.3366 | 53.1086 | 43.6212 | 31.8651 | 18.2529 | 2.6812 | 0 | 0 | 0 | 0 | 0 | 0
6 | 38 | 0 | 0 | 0 | 0 | 0 | 2.3402 | 17.4453 | 30.5293 | 42.7623 | 52.655 | 58.2928 | 59.8884 | 59.1438 | 54.7825 | 44.9961 | 32.8695 | 18.8282 | 2.7657 | 0 | 0 | 0 | 0 | 0 | 0 | 6
6 | 39 | 0 | 0 | 0 | 0 | 0 | 2.2687 | 16.9122 | 29.5964 | 41.4556 | 51.0461 | 56.5116 | 58.0585 | 57.3366 | 53.1086 | 43.6212 | 31.8651 | 18.2529 | 2.6812 | 0 | 0 | 0 | 0 | 0 | 0
6 | 40 | 0 | 0 | 0 | 0 | 0 | 2.1842 | 16.2823 | 28.494 | 39.9114 | 49.1447 | 54.4066 | 55.8959 | 55.2009 | 51.1303 | 41.9964 | 30.6782 | 17.5729 | 2.5813 | 0 | 0 | 0 | 0 | 0 | 0 | 6
6 | 41 | 0 | 0 | 0 | 0 | 0 | 2.2687 | 16.9122 | 29.5964 | 41.4556 | 51.0461 | 56.5116 | 58.0585 | 57.3366 | 53.1086 | 43.6212 | 31.8651 | 18.2529 | 2.6812 | 0 | 0 | 0 | 0 | 0 | 0
6 | 42 | 0 | 0 | 0 | 0 | 0 | 2.0282 | 15.1193 | 26.4587 | 37.0606 | 45.6343 | 50.5204 | 51.9033 | 51.258 | 47.4782 | 38.9966 | 28.4869 | 16.3177 | 2.397 | 0 | 0 | 0 | 0 | 0 | 0 | 6
7 | 43 | 0 | 0 | 0 | 0 | 0 | 0.85099 | 9.5311 | 17.2751 | 23.9979 | 30.2101 | 33.9545 | 34.5502 | 34.0396 | 31.1462 | 25.6148 | 17.7857 | 10.5523 | 1.5318 | 0 | 0 | 0 | 0 | 0 | 0 | 7
7 | 44 | 0 | 0 | 0 | 0 | 0 | 0.78598 | 8.803 | 15.9555 | 22.1647 | 27.9024 | 31.3608 | 31.9109 | 31.4394 | 28.767 | 23.6581 | 16.4271 | 9.7462 | 1.4148 | 0 | 0 | 0 | 0 | 0 | 0
7 | 45 | 0 | 0 | 0 | 0 | 0 | 0.78007 | 8.7368 | 15.8355 | 21.9981 | 27.6926 | 31.125 | 31.671 | 31.203 | 28.5507 | 23.4802 | 16.3036 | 9.6729 | 1.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 7
7 | 46 | 0 | 0 | 0 | 0 | 0 | 0.78598 | 8.803 | 15.9555 | 22.1647 | 27.9024 | 31.3608 | 31.9109 | 31.4394 | 28.767 | 23.6581 | 16.4271 | 9.7462 | 1.4148 | 0 | 0 | 0 | 0 | 0 | 0
7 | 47 | 0 | 0 | 0 | 0 | 0 | 0.76432 | 8.5603 | 15.5156 | 21.5537 | 27.1332 | 30.4962 | 31.0312 | 30.5726 | 27.9739 | 23.0059 | 15.9742 | 9.4775 | 1.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 7
7 | 48 | 0 | 0 | 0 | 0 | 0 | 0.78598 | 8.803 | 15.9555 | 22.1647 | 27.9024 | 31.3608 | 31.9109 | 31.4394 | 28.767 | 23.6581 | 16.4271 | 9.7462 | 1.4148 | 0 | 0 | 0 | 0 | 0 | 0
7 | 49 | 0 | 0 | 0 | 0 | 0 | 0.74856 | 8.3838 | 15.1957 | 21.1093 | 26.5737 | 29.8674 | 30.3914 | 29.9422 | 27.3972 | 22.5315 | 15.6448 | 9.2821 | 1.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 7
8 | 50 | 0 | 0 | 0 | 0 | 0 | 0.21984 | 8.4272 | 15.6086 | 19.7855 | 23.6693 | 25.5013 | 25.3548 | 24.9884 | 23.3029 | 19.126 | 13.7766 | 8.7203 | 1.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 8
8 | 51 | 0 | 0 | 0 | 0 | 0 | 0.21511 | 8.2459 | 15.2729 | 19.36 | 23.1603 | 24.9529 | 24.8095 | 24.451 | 22.8018 | 18.7147 | 13.4803 | 8.5328 | 1.219 | 0 | 0 | 0 | 0 | 0 | 0 | 8
8 | 52 | 0 | 0 | 0 | 0 | 0 | 0.21889 | 8.3909 | 15.5414 | 19.7004 | 23.5675 | 25.3917 | 25.2457 | 24.8809 | 23.2027 | 19.0437 | 13.7173 | 8.6828 | 1.2404 | 0 | 0 | 0 | 0 | 0 | 0
8 | 53 | 0 | 0 | 0 | 0 | 0 | 0.21038 | 8.0647 | 14.9372 | 18.9345 | 22.6513 | 24.4045 | 24.2642 | 23.9136 | 22.3007 | 18.3034 | 13.184 | 8.3452 | 1.1922 | 0 | 0 | 0 | 0 | 0 | 0 | 8
8 | 54 | 0 | 0 | 0 | 0 | 0 | 0.21889 | 8.3909 | 15.5414 | 19.7004 | 23.5675 | 25.3917 | 25.2457 | 24.8809 | 23.2027 | 19.0437 | 13.7173 | 8.6828 | 1.2404 | 0 | 0 | 0 | 0 | 0 | 0
8 | 55 | 0 | 0 | 0 | 0 | 0 | 0.21984 | 8.4272 | 15.6086 | 19.7855 | 23.6693 | 25.5013 | 25.3548 | 24.9884 | 23.3029 | 19.126 | 13.7766 | 8.7203 | 1.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 8
8 | 56 | 0 | 0 | 0 | 0 | 0 | 0.22929 | 8.7896 | 16.2799 | 20.6365 | 24.6874 | 26.5982 | 26.4453 | 26.0631 | 24.3052 | 19.9486 | 14.3691 | 9.0954 | 1.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 8
9 | 57 | 0 | 0 | 0 | 0 | 0 | 0.31833 | 11.3804 | 20.6917 | 27.9337 | 34.0617 | 35.4942 | 34.3004 | 33.1067 | 30.4804 | 24.7504 | 17.8267 | 8.7542 | 0.31833 | 0 | 0 | 0 | 0 | 0 | 0 | 9
9 | 58 | 0 | 0 | 0 | 0 | 0 | 0.33961 | 12.141 | 22.0745 | 29.8006 | 36.3381 | 37.8663 | 36.5928 | 35.3192 | 32.5175 | 26.4045 | 19.0181 | 9.3392 | 0.33961 | 0 | 0 | 0 | 0 | 0 | 0
9 | 59 | 0 | 0 | 0 | 0 | 0 | 0.33094 | 11.8311 | 21.5111 | 29.04 | 35.4106 | 36.8999 | 35.6588 | 34.4178 | 31.6876 | 25.7306 | 18.5327 | 9.1009 | 0.33094 | 0 | 0 | 0 | 0 | 0 | 0 | 9
9 | 60 | 0 | 0 | 0 | 0 | 0 | 0.33961 | 12.141 | 22.0745 | 29.8006 | 36.3381 | 37.8663 | 36.5928 | 35.3192 | 32.5175 | 26.4045 | 19.0181 | 9.3392 | 0.33961 | 0 | 0 | 0 | 0 | 0 | 0
9 | 61 | 0 | 0 | 0 | 0 | 0 | 0.3467 | 12.3945 | 22.5355 | 30.4229 | 37.0969 | 38.657 | 37.3569 | 36.0568 | 33.1965 | 26.9559 | 19.4152 | 9.5342 | 0.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 9
9 | 62 | 0 | 0 | 0 | 0 | 0 | 0.33961 | 12.141 | 22.0745 | 29.8006 | 36.3381 | 37.8663 | 36.5928 | 35.3192 | 32.5175 | 26.4045 | 19.0181 | 9.3392 | 0.33961 | 0 | 0 | 0 | 0 | 0 | 0
9 | 63 | 0 | 0 | 0 | 0 | 0 | 0.36246 | 12.9579 | 23.5598 | 31.8058 | 38.7831 | 40.4141 | 39.0549 | 37.6957 | 34.7054 | 28.1812 | 20.2977 | 9.9676 | 0.36246 | 0 | 0 | 0 | 0 | 0 | 0 | 9
10 | 64 | 0 | 0 | 0 | 0 | 0 | 0.47277 | 15.9797 | 30.352 | 41.4148 | 50.0193 | 51.9104 | 50.6812 | 47.3718 | 42.8332 | 35.3634 | 24.1114 | 7.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
10 | 65 | 0 | 0 | 0 | 0 | 0 | 0.50153 | 16.9518 | 32.1984 | 43.9343 | 53.0621 | 55.0683 | 53.7643 | 50.2536 | 45.4389 | 37.5146 | 25.5782 | 7.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 66 | 0 | 0 | 0 | 0 | 0 | 0.49247 | 16.6455 | 31.6166 | 43.1405 | 52.1034 | 54.0733 | 52.7929 | 49.3456 | 44.6179 | 36.8368 | 25.116 | 7.3871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
10 | 67 | 0 | 0 | 0 | 0 | 0 | 0.51217 | 17.3113 | 32.8813 | 44.8661 | 54.1876 | 56.2363 | 54.9046 | 51.3194 | 46.4026 | 38.3103 | 26.1207 | 7.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
10 | 68 | 0 | 0 | 0 | 0 | 0 | 0.50153 | 16.9518 | 32.1984 | 43.9343 | 53.0621 | 55.0683 | 53.7643 | 50.2536 | 45.4389 | 37.5146 | 25.5782 | 7.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 69 | 0 | 0 | 0 | 0 | 0 | 0.51414 | 17.3779 | 33.0078 | 45.0386 | 54.396 | 56.4526 | 55.1158 | 51.5168 | 46.5811 | 38.4577 | 26.2211 | 7.7121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
10 | 70 | 0 | 0 | 0 | 0 | 0 | 0.51611 | 17.4445 | 33.1342 | 45.2112 | 54.6044 | 56.6688 | 55.327 | 51.7142 | 46.7595 | 38.605 | 26.3216 | 7.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
11 | 71 | 0 | 0 | 0 | 0 | 0 | 0.10362 | 17.3039 | 35.0222 | 47.0416 | 56.0562 | 59.89 | 59.3719 | 55.849 | 49.9429 | 41.1355 | 28.2871 | 5.9061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11
11 | 72 | 0 | 0 | 0 | 0 | 0 | 0.10391 | 17.3532 | 35.1221 | 47.1758 | 56.2161 | 60.0608 | 59.5412 | 56.0082 | 50.0853 | 41.2528 | 28.3678 | 5.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 73 | 0 | 0 | 0 | 0 | 0 | 0.10401 | 17.3697 | 35.1553 | 47.2205 | 56.2694 | 60.1177 | 59.5977 | 56.0613 | 50.1328 | 41.2919 | 28.3947 | 5.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11
11 | 74 | 0 | 0 | 0 | 0 | 0 | 0.10391 | 17.3532 | 35.1221 | 47.1758 | 56.2161 | 60.0608 | 59.5412 | 56.0082 | 50.0853 | 41.2528 | 28.3678 | 5.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 75 | 0 | 0 | 0 | 0 | 0 | 0.10401 | 17.3697 | 35.1553 | 47.2205 | 56.2694 | 60.1177 | 59.5977 | 56.0613 | 50.1328 | 41.2919 | 28.3947 | 5.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11
11 | 76 | 0 | 0 | 0 | 0 | 0 | 0.10391 | 17.3532 | 35.1221 | 47.1758 | 56.2161 | 60.0608 | 59.5412 | 56.0082 | 50.0853 | 41.2528 | 28.3678 | 5.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 77 | 0 | 0 | 0 | 0 | 0 | 0.10401 | 17.3697 | 35.1553 | 47.2205 | 56.2694 | 60.1177 | 59.5977 | 56.0613 | 50.1328 | 41.2919 | 28.3947 | 5.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11
12 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9048 | 32.6591 | 45.3483 | 53.5651 | 57.3095 | 57.7255 | 55.4373 | 50.0288 | 42.124 | 30.9949 | 9.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
12 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9766 | 32.956 | 45.7606 | 54.0521 | 57.8304 | 58.2503 | 55.9413 | 50.4836 | 42.507 | 31.2767 | 9.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9766 | 32.956 | 45.7606 | 54.0521 | 57.8304 | 58.2503 | 55.9413 | 50.4836 | 42.507 | 31.2767 | 9.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9048 | 32.6591 | 45.3483 | 53.5651 | 57.3095 | 57.7255 | 55.4373 | 50.0288 | 42.124 | 30.9949 | 9.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
12 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0006 | 33.055 | 45.898 | 54.2144 | 58.0041 | 58.4252 | 56.1092 | 50.6352 | 42.6346 | 31.3706 | 9.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12
12 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9766 | 32.956 | 45.7606 | 54.0521 | 57.8304 | 58.2503 | 55.9413 | 50.4836 | 42.507 | 31.2767 | 9.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0964 | 33.4508 | 46.4477 | 54.8636 | 58.6988 | 59.1249 | 56.7812 | 51.2416 | 43.1452 | 31.7463 | 9.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12

## Hourly Wind Profile
Example of one direction e.g. N there will be another document explaining how I got this data from DTU's wind atlas
WN |  | Hours | [23 empty] | WS |  | Hours
Month | Week | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Month | Week | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
1 | 1 | 88.0901 | 89.0397 | 88.0901 | 88.0901 | 88.0901 | 89.0397 | 89.9893 | 90.939 | 92.8382 | 91.8886 | 90.939 | 90.939 | 89.9893 | 89.9893 | 89.0397 | 89.0397 | 88.0901 | 88.0901 | 88.0901 | 89.0397 | 89.9893 | 90.939 | 89.9893 | 88.0901 | 1 | 1 | 62.7124 | 60.3773 | 59.5989 | 59.5989 | 60.3773 | 61.1557 | 61.934 | 61.934 | 62.7124 | 62.7124 | 61.934 | 61.934 | 61.1557 | 61.1557 | 60.3773 | 60.3773 | 59.5989 | 60.3773 | 61.1557 | 61.1557 | 61.1557 | 61.1557 | 60.3773 | 60.3773
1 | 2 | 89.6241 | 90.5859 | 89.6241 | 89.6241 | 89.6241 | 90.5859 | 91.5477 | 92.5095 | 94.4331 | 93.4713 | 92.5095 | 92.5095 | 91.5477 | 91.5477 | 90.5859 | 90.5859 | 89.6241 | 89.6241 | 89.6241 | 90.5859 | 91.5477 | 92.5095 | 91.5477 | 89.6241 | 1 | 2 | 64.8752 | 62.4822 | 61.6845 | 61.6845 | 62.4822 | 63.2799 | 64.0775 | 64.0775 | 64.8752 | 64.8752 | 64.0775 | 64.0775 | 63.2799 | 63.2799 | 62.4822 | 62.4822 | 61.6845 | 62.4822 | 63.2799 | 63.2799 | 63.2799 | 63.2799 | 62.4822 | 62.4822
1 | 3 | 91.1581 | 92.1321 | 91.1581 | 91.1581 | 91.1581 | 92.1321 | 93.1061 | 94.08 | 96.028 | 95.054 | 94.08 | 94.08 | 93.1061 | 93.1061 | 92.1321 | 92.1321 | 91.1581 | 91.1581 | 91.1581 | 92.1321 | 93.1061 | 94.08 | 93.1061 | 91.1581 | 1 | 3 | 67.038 | 64.587 | 63.7701 | 63.7701 | 64.587 | 65.404 | 66.221 | 66.221 | 67.038 | 67.038 | 66.221 | 66.221 | 65.404 | 65.404 | 64.587 | 64.587 | 63.7701 | 64.587 | 65.404 | 65.404 | 65.404 | 65.404 | 64.587 | 64.587
1 | 4 | 91.6375 | 92.6153 | 91.6375 | 91.6375 | 91.6375 | 92.6153 | 93.5931 | 94.5708 | 96.5264 | 95.5486 | 94.5708 | 94.5708 | 93.5931 | 93.5931 | 92.6153 | 92.6153 | 91.6375 | 91.6375 | 91.6375 | 92.6153 | 93.5931 | 94.5708 | 93.5931 | 91.6375 | 1 | 4 | 69.3256 | 66.8134 | 65.9759 | 65.9759 | 66.8134 | 67.6508 | 68.4882 | 68.4882 | 69.3256 | 69.3256 | 68.4882 | 68.4882 | 67.6508 | 67.6508 | 66.8134 | 66.8134 | 65.9759 | 66.8134 | 67.6508 | 67.6508 | 67.6508 | 67.6508 | 66.8134 | 66.8134
1 | 5 | 92.1169 | 93.0985 | 92.1169 | 92.1169 | 92.1169 | 93.0985 | 94.08 | 95.0616 | 97.0248 | 96.0432 | 95.0616 | 95.0616 | 94.08 | 94.08 | 93.0985 | 93.0985 | 92.1169 | 92.1169 | 92.1169 | 93.0985 | 94.08 | 95.0616 | 94.08 | 92.1169 | 1 | 5 | 71.6132 | 69.0397 | 68.1818 | 68.1818 | 69.0397 | 69.8975 | 70.7553 | 70.7553 | 71.6132 | 71.6132 | 70.7553 | 70.7553 | 69.8975 | 69.8975 | 69.0397 | 69.0397 | 68.1818 | 69.0397 | 69.8975 | 69.8975 | 69.8975 | 69.8975 | 69.0397 | 69.0397
2 | 6 | 92.5963 | 92.5963 | 93.5816 | 93.5816 | 92.5963 | 92.5963 | 94.567 | 95.5524 | 96.5378 | 98.5086 | 99.494 | 99.494 | 98.5086 | 97.5232 | 97.5232 | 95.5524 | 95.5524 | 96.5378 | 97.5232 | 98.5086 | 98.5086 | 99.494 | 98.5086 | 96.5378 | 2 | 6 | 82.6835 | 81.8052 | 79.1704 | 80.0486 | 80.0486 | 80.0486 | 80.9269 | 81.8052 | 82.6835 | 82.6835 | 80.9269 | 80.0486 | 80.0486 | 80.9269 | 80.9269 | 80.9269 | 81.8052 | 81.8052 | 82.6835 | 84.44 | 85.3183 | 86.1965 | 87.0748 | 86.1965
2 | 7 | 93.0756 | 93.0756 | 94.0648 | 94.0648 | 93.0756 | 93.0756 | 95.054 | 96.0432 | 97.0324 | 99.0108 | 100 | 100 | 99.0108 | 98.0216 | 98.0216 | 96.0432 | 96.0432 | 97.0324 | 98.0216 | 99.0108 | 99.0108 | 100 | 99.0108 | 97.0324 | 2 | 7 | 85.1753 | 84.2766 | 81.5805 | 82.4792 | 82.4792 | 82.4792 | 83.3779 | 84.2766 | 85.1753 | 85.1753 | 83.3779 | 82.4792 | 82.4792 | 83.3779 | 83.3779 | 83.3779 | 84.2766 | 84.2766 | 85.1753 | 86.9727 | 87.8714 | 88.7701 | 89.6687 | 88.7701
2 | 8 | 89.4803 | 89.4803 | 90.441 | 90.441 | 89.4803 | 89.4803 | 91.4016 | 92.3623 | 93.3229 | 95.2443 | 96.2049 | 96.2049 | 95.2443 | 94.2836 | 94.2836 | 92.3623 | 92.3623 | 93.3229 | 94.2836 | 95.2443 | 95.2443 | 96.2049 | 95.2443 | 93.3229 | 2 | 8 | 85.1753 | 84.2766 | 81.5805 | 82.4792 | 82.4792 | 82.4792 | 83.3779 | 84.2766 | 85.1753 | 85.1753 | 83.3779 | 82.4792 | 82.4792 | 83.3779 | 83.3779 | 83.3779 | 84.2766 | 84.2766 | 85.1753 | 86.9727 | 87.8714 | 88.7701 | 89.6687 | 88.7701
3 | 9 | 72.8352 | 71.9031 | 71.9031 | 72.8352 | 72.8352 | 72.8352 | 72.8352 | 73.7673 | 74.6994 | 76.5637 | 77.4958 | 77.4958 | 76.5637 | 75.6316 | 75.6316 | 77.4958 | 77.4958 | 78.4279 | 77.4958 | 77.4958 | 78.4279 | 76.5637 | 76.5637 | 74.6994 | 3 | 9 | 85.1753 | 85.1753 | 84.2766 | 83.3779 | 81.5805 | 81.5805 | 81.5805 | 82.4792 | 83.3779 | 83.3779 | 83.3779 | 84.2766 | 84.2766 | 85.1753 | 84.2766 | 84.2766 | 83.3779 | 84.2766 | 85.1753 | 86.074 | 86.074 | 86.074 | 86.074 | 86.074
3 | 10 | 69.6393 | 68.7357 | 68.7357 | 69.6393 | 69.6393 | 69.6393 | 69.6393 | 70.5429 | 71.4465 | 73.2537 | 74.1573 | 74.1573 | 73.2537 | 72.3501 | 72.3501 | 74.1573 | 74.1573 | 75.0609 | 74.1573 | 74.1573 | 75.0609 | 73.2537 | 73.2537 | 71.4465 | 3 | 10 | 85.1753 | 85.1753 | 84.2766 | 83.3779 | 81.5805 | 81.5805 | 81.5805 | 82.4792 | 83.3779 | 83.3779 | 83.3779 | 84.2766 | 84.2766 | 85.1753 | 84.2766 | 84.2766 | 83.3779 | 84.2766 | 85.1753 | 86.074 | 86.074 | 86.074 | 86.074 | 86.074
3 | 11 | 66.4435 | 65.5684 | 65.5684 | 66.4435 | 66.4435 | 66.4435 | 66.4435 | 67.3185 | 68.1936 | 69.9437 | 70.8187 | 70.8187 | 69.9437 | 69.0686 | 69.0686 | 70.8187 | 70.8187 | 71.6938 | 70.8187 | 70.8187 | 71.6938 | 69.9437 | 69.9437 | 68.1936 | 3 | 11 | 85.1753 | 85.1753 | 84.2766 | 83.3779 | 81.5805 | 81.5805 | 81.5805 | 82.4792 | 83.3779 | 83.3779 | 83.3779 | 84.2766 | 84.2766 | 85.1753 | 84.2766 | 84.2766 | 83.3779 | 84.2766 | 85.1753 | 86.074 | 86.074 | 86.074 | 86.074 | 86.074
3 | 12 | 64.739 | 63.8792 | 63.8792 | 64.739 | 64.739 | 64.739 | 64.739 | 65.5988 | 66.4587 | 68.1784 | 69.0382 | 69.0382 | 68.1784 | 67.3185 | 67.3185 | 69.0382 | 69.0382 | 69.898 | 69.0382 | 69.0382 | 69.898 | 68.1784 | 68.1784 | 66.4587 | 3 | 12 | 84.9488 | 84.9488 | 84.0519 | 83.1551 | 81.3614 | 81.3614 | 81.3614 | 82.2582 | 83.1551 | 83.1551 | 83.1551 | 84.0519 | 84.0519 | 84.9488 | 84.0519 | 84.0519 | 83.1551 | 84.0519 | 84.9488 | 85.8456 | 85.8456 | 85.8456 | 85.8456 | 85.8456
3 | 13 | 63.0345 | 62.1899 | 62.1899 | 63.0345 | 63.0345 | 63.0345 | 63.0345 | 63.8792 | 64.7238 | 66.413 | 67.2576 | 67.2576 | 66.413 | 65.5684 | 65.5684 | 67.2576 | 67.2576 | 68.1023 | 67.2576 | 67.2576 | 68.1023 | 66.413 | 66.413 | 64.7238 | 3 | 13 | 84.7222 | 84.7222 | 83.8272 | 82.9323 | 81.1423 | 81.1423 | 81.1423 | 82.0373 | 82.9323 | 82.9323 | 82.9323 | 83.8272 | 83.8272 | 84.7222 | 83.8272 | 83.8272 | 82.9323 | 83.8272 | 84.7222 | 85.6172 | 85.6172 | 85.6172 | 85.6172 | 85.6172
4 | 14 | 55.5243 | 53.8655 | 53.0361 | 53.0361 | 53.0361 | 53.0361 | 53.8655 | 54.6949 | 54.6949 | 55.5243 | 56.3537 | 56.3537 | 56.3537 | 56.3537 | 57.1831 | 58.0125 | 58.8419 | 59.6713 | 60.5007 | 61.3301 | 61.3301 | 62.1595 | 61.3301 | 59.6713 | 4 | 14 | 88.9613 | 86.2819 | 84.4957 | 82.7094 | 80.9232 | 80.0301 | 80.0301 | 79.137 | 79.137 | 79.137 | 79.137 | 80.9232 | 81.8163 | 81.8163 | 80.9232 | 80.0301 | 79.137 | 80.9232 | 81.8163 | 83.6026 | 86.2819 | 88.0682 | 88.9613 | 89.8544
4 | 15 | 53.9263 | 52.298 | 51.4838 | 51.4838 | 51.4838 | 51.4838 | 52.298 | 53.1122 | 53.1122 | 53.9263 | 54.7405 | 54.7405 | 54.7405 | 54.7405 | 55.5547 | 56.3689 | 57.1831 | 57.9973 | 58.8114 | 59.6256 | 59.6256 | 60.4398 | 59.6256 | 57.9973 | 4 | 15 | 88.7255 | 86.0517 | 84.2692 | 82.4866 | 80.7041 | 79.8128 | 79.8128 | 78.9216 | 78.9216 | 78.9216 | 78.9216 | 80.7041 | 81.5954 | 81.5954 | 80.7041 | 79.8128 | 78.9216 | 80.7041 | 81.5954 | 83.3779 | 86.0517 | 87.8342 | 88.7255 | 89.6168
4 | 16 | 53.9263 | 52.298 | 51.4838 | 51.4838 | 51.4838 | 51.4838 | 52.298 | 53.1122 | 53.1122 | 53.9263 | 54.7405 | 54.7405 | 54.7405 | 54.7405 | 55.5547 | 56.3689 | 57.1831 | 57.9973 | 58.8114 | 59.6256 | 59.6256 | 60.4398 | 59.6256 | 57.9973 | 4 | 16 | 89.8574 | 87.1569 | 85.3565 | 83.5561 | 81.7558 | 80.8556 | 80.8556 | 79.9554 | 79.9554 | 79.9554 | 79.9554 | 81.7558 | 82.656 | 82.656 | 81.7558 | 80.8556 | 79.9554 | 81.7558 | 82.656 | 84.4563 | 87.1569 | 88.9572 | 89.8574 | 90.7576
4 | 17 | 53.9263 | 52.298 | 51.4838 | 51.4838 | 51.4838 | 51.4838 | 52.298 | 53.1122 | 53.1122 | 53.9263 | 54.7405 | 54.7405 | 54.7405 | 54.7405 | 55.5547 | 56.3689 | 57.1831 | 57.9973 | 58.8114 | 59.6256 | 59.6256 | 60.4398 | 59.6256 | 57.9973 | 4 | 17 | 90.9893 | 88.262 | 86.4439 | 84.6257 | 82.8075 | 81.8984 | 81.8984 | 80.9893 | 80.9893 | 80.9893 | 80.9893 | 82.8075 | 83.7166 | 83.7166 | 82.8075 | 81.8984 | 80.9893 | 82.8075 | 83.7166 | 85.5348 | 88.262 | 90.0802 | 90.9893 | 91.8984
5 | 18 | 53.9263 | 52.298 | 51.4838 | 50.6696 | 50.6696 | 51.4838 | 52.298 | 53.1122 | 54.7405 | 54.7405 | 56.3689 | 56.3689 | 56.3689 | 57.1831 | 57.9973 | 59.6256 | 59.6256 | 60.4398 | 61.254 | 60.4398 | 59.6256 | 58.8114 | 57.1831 | 54.7405 | 5 | 18 | 94.8752 | 93.0392 | 91.2032 | 90.2852 | 90.2852 | 90.2852 | 90.2852 | 90.2852 | 90.2852 | 89.3672 | 88.4492 | 87.5312 | 86.6132 | 86.6132 | 86.6132 | 88.4492 | 91.2032 | 93.0392 | 94.8752 | 95.7932 | 97.6292 | 97.6292 | 97.6292 | 96.7112
5 | 19 | 53.9263 | 52.298 | 51.4838 | 50.6696 | 50.6696 | 51.4838 | 52.298 | 53.1122 | 54.7405 | 54.7405 | 56.3689 | 56.3689 | 56.3689 | 57.1831 | 57.9973 | 59.6256 | 59.6256 | 60.4398 | 61.254 | 60.4398 | 59.6256 | 58.8114 | 57.1831 | 54.7405 | 5 | 19 | 96.0339 | 94.18 | 92.3262 | 91.3993 | 91.3993 | 91.3993 | 91.3993 | 91.3993 | 91.3993 | 90.4724 | 89.5455 | 88.6185 | 87.6916 | 87.6916 | 87.6916 | 89.5455 | 92.3262 | 94.18 | 96.0339 | 96.9608 | 98.8146 | 98.8146 | 98.8146 | 97.8877
5 | 20 | 53.9263 | 52.298 | 51.4838 | 50.6696 | 50.6696 | 51.4838 | 52.298 | 53.1122 | 54.7405 | 54.7405 | 56.3689 | 56.3689 | 56.3689 | 57.1831 | 57.9973 | 59.6256 | 59.6256 | 60.4398 | 61.254 | 60.4398 | 59.6256 | 58.8114 | 57.1831 | 54.7405 | 5 | 20 | 97.1925 | 95.3209 | 93.4492 | 92.5134 | 92.5134 | 92.5134 | 92.5134 | 92.5134 | 92.5134 | 91.5775 | 90.6417 | 89.7059 | 88.7701 | 88.7701 | 88.7701 | 90.6417 | 93.4492 | 95.3209 | 97.1925 | 98.1283 | 100 | 100 | 100 | 99.0642
5 | 21 | 51.13 | 49.5549 | 48.7673 | 47.9798 | 47.9798 | 48.7673 | 49.5549 | 50.3424 | 51.9175 | 51.9175 | 53.4926 | 53.4926 | 53.4926 | 54.2802 | 55.0677 | 56.6428 | 56.6428 | 57.4304 | 58.2179 | 57.4304 | 56.6428 | 55.8553 | 54.2802 | 51.9175 | 5 | 21 | 94.0545 | 92.2311 | 90.4078 | 89.4961 | 89.4961 | 89.4961 | 89.4961 | 89.4961 | 89.4961 | 88.5844 | 87.6727 | 86.761 | 85.8493 | 85.8493 | 85.8493 | 87.6727 | 90.4078 | 92.2311 | 94.0545 | 94.9662 | 96.7896 | 96.7896 | 96.7896 | 95.8779
5 | 22 | 48.3336 | 46.8117 | 46.0508 | 45.2899 | 45.2899 | 46.0508 | 46.8117 | 47.5727 | 49.0945 | 49.0945 | 50.6163 | 50.6163 | 50.6163 | 51.3773 | 52.1382 | 53.66 | 53.66 | 54.4209 | 55.1819 | 54.4209 | 53.66 | 52.8991 | 51.3773 | 49.0945 | 5 | 22 | 90.9165 | 89.1414 | 87.3663 | 86.4788 | 86.4788 | 86.4788 | 86.4788 | 86.4788 | 86.4788 | 85.5912 | 84.7037 | 83.8161 | 82.9286 | 82.9286 | 82.9286 | 84.7037 | 87.3663 | 89.1414 | 90.9165 | 91.8041 | 93.5792 | 93.5792 | 93.5792 | 92.6916
6 | 23 | 36.7258 | 35.9915 | 34.5229 | 34.5229 | 33.7886 | 33.7886 | 34.5229 | 34.5229 | 35.2572 | 35.9915 | 36.7258 | 37.4601 | 36.7258 | 36.7258 | 37.4601 | 37.4601 | 37.4601 | 38.1943 | 39.6629 | 38.9286 | 38.1943 | 37.4601 | 36.7258 | 35.9915 | 6 | 23 | 73.1005 | 71.3737 | 70.5102 | 70.5102 | 70.5102 | 70.5102 | 72.2371 | 74.8273 | 76.5541 | 75.6907 | 73.9639 | 73.1005 | 70.5102 | 70.5102 | 70.5102 | 71.3737 | 72.2371 | 73.9639 | 74.8273 | 75.6907 | 76.5541 | 78.281 | 78.281 | 77.4176
6 | 24 | 34.249 | 33.5413 | 32.126 | 32.126 | 31.4184 | 31.4184 | 32.126 | 32.126 | 32.8337 | 33.5413 | 34.249 | 34.9566 | 34.249 | 34.249 | 34.9566 | 34.9566 | 34.9566 | 35.6643 | 37.0796 | 36.3719 | 35.6643 | 34.9566 | 34.249 | 33.5413 | 6 | 24 | 70.3728 | 68.6943 | 67.855 | 67.855 | 67.855 | 67.855 | 69.5336 | 72.0514 | 73.7299 | 72.8907 | 71.2121 | 70.3728 | 67.855 | 67.855 | 67.855 | 68.6943 | 69.5336 | 71.2121 | 72.0514 | 72.8907 | 73.7299 | 75.4085 | 75.4085 | 74.5692
6 | 25 | 30.003 | 29.341 | 28.017 | 28.017 | 27.355 | 27.355 | 28.017 | 28.017 | 28.679 | 29.341 | 30.003 | 30.665 | 30.003 | 30.003 | 30.665 | 30.665 | 30.665 | 31.327 | 32.651 | 31.989 | 31.327 | 30.665 | 30.003 | 29.341 | 6 | 25 | 62.1899 | 60.6562 | 59.8893 | 59.8893 | 59.8893 | 59.8893 | 61.4231 | 63.7236 | 65.2574 | 64.4905 | 62.9568 | 62.1899 | 59.8893 | 59.8893 | 59.8893 | 60.6562 | 61.4231 | 62.9568 | 63.7236 | 64.4905 | 65.2574 | 66.7911 | 66.7911 | 66.0242
6 | 26 | 25.7571 | 25.1408 | 23.9081 | 23.9081 | 23.2917 | 23.2917 | 23.9081 | 23.9081 | 24.5244 | 25.1408 | 25.7571 | 26.3735 | 25.7571 | 25.7571 | 26.3735 | 26.3735 | 26.3735 | 26.9898 | 28.2225 | 27.6061 | 26.9898 | 26.3735 | 25.7571 | 25.1408 | 6 | 26 | 54.007 | 52.6181 | 51.9236 | 51.9236 | 51.9236 | 51.9236 | 53.3125 | 55.3959 | 56.7848 | 56.0903 | 54.7014 | 54.007 | 51.9236 | 51.9236 | 51.9236 | 52.6181 | 53.3125 | 54.7014 | 55.3959 | 56.0903 | 56.7848 | 58.1736 | 58.1736 | 57.4792
7 | 27 | 5.5319 | 5.5319 | 5.5319 | 5.5319 | 5.5319 | 6.6733 | 6.6733 | 7.244 | 7.244 | 7.244 | 8.3853 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 10.0974 | 8.956 | 8.3853 | 7.244 | 6.1026 | 5.5319 | 7 | 27 | 22.809 | 22.809 | 22.1869 | 20.9429 | 19.6988 | 20.3209 | 21.5649 | 22.1869 | 21.5649 | 20.9429 | 20.9429 | 20.9429 | 20.3209 | 19.0768 | 19.0768 | 19.0768 | 19.0768 | 20.3209 | 20.9429 | 22.809 | 24.6751 | 25.9191 | 27.7852 | 28.4072
7 | 28 | 2.5643 | 2.5643 | 2.5643 | 2.5643 | 2.5643 | 3.6144 | 3.6144 | 4.1394 | 4.1394 | 4.1394 | 5.1895 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.7646 | 5.7145 | 5.1895 | 4.1394 | 3.0893 | 2.5643 | 7 | 28 | 17.3054 | 17.3054 | 16.7558 | 15.6566 | 14.5573 | 15.107 | 16.2062 | 16.7558 | 16.2062 | 15.6566 | 15.6566 | 15.6566 | 15.107 | 14.0077 | 14.0077 | 14.0077 | 14.0077 | 15.107 | 15.6566 | 17.3054 | 18.9542 | 20.0535 | 21.7023 | 22.2519
7 | 29 | 2.4654 | 2.4654 | 2.4654 | 2.4654 | 2.4654 | 3.5124 | 3.5124 | 4.0359 | 4.0359 | 4.0359 | 5.0829 | 6.13 | 6.13 | 6.13 | 6.13 | 6.13 | 6.13 | 6.13 | 6.6535 | 5.6065 | 5.0829 | 4.0359 | 2.9889 | 2.4654 | 7 | 29 | 15.8378 | 15.8378 | 15.3075 | 14.2469 | 13.1863 | 13.7166 | 14.7772 | 15.3075 | 14.7772 | 14.2469 | 14.2469 | 14.2469 | 13.7166 | 12.656 | 12.656 | 12.656 | 12.656 | 13.7166 | 14.2469 | 15.8378 | 17.4287 | 18.4893 | 20.0802 | 20.6105
7 | 30 | 2.3665 | 2.3665 | 2.3665 | 2.3665 | 2.3665 | 3.4104 | 3.4104 | 3.9324 | 3.9324 | 3.9324 | 4.9764 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.5424 | 5.4984 | 4.9764 | 3.9324 | 2.8884 | 2.3665 | 7 | 30 | 14.3702 | 14.3702 | 13.8592 | 12.8372 | 11.8152 | 12.3262 | 13.3482 | 13.8592 | 13.3482 | 12.8372 | 12.8372 | 12.8372 | 12.3262 | 11.3042 | 11.3042 | 11.3042 | 11.3042 | 12.3262 | 12.8372 | 14.3702 | 15.9031 | 16.9251 | 18.4581 | 18.9691
8 | 31 | 0.18566 | 0.18566 | 0.70613 | 1.7471 | 3.3085 | 3.8289 | 3.8289 | 4.3494 | 4.3494 | 4.8699 | 5.3904 | 5.9108 | 5.9108 | 6.4313 | 6.9518 | 6.4313 | 5.9108 | 5.3904 | 4.3494 | 3.3085 | 2.788 | 2.788 | 2.2675 | 2.2675 | 8 | 31 | 7.9857 | 7.4941 | 6.5107 | 6.019 | 7.0024 | 8.4774 | 8.9691 | 9.4608 | 8.9691 | 7.0024 | 5.5273 | 5.0357 | 4.0523 | 3.5606 | 3.0689 | 3.0689 | 2.5772 | 2.0856 | 3.0689 | 4.0523 | 4.544 | 5.0357 | 5.5273 | 6.019
8 | 32 | 0.092832 | 0.092832 | 0.61178 | 1.6497 | 3.2065 | 3.7255 | 3.7255 | 4.2444 | 4.2444 | 4.7634 | 5.2823 | 5.8012 | 5.8012 | 6.3202 | 6.8391 | 6.3202 | 5.8012 | 5.2823 | 4.2444 | 3.2065 | 2.6876 | 2.6876 | 2.1686 | 2.1686 | 8 | 32 | 6.7112 | 6.2389 | 5.2941 | 4.8217 | 5.7665 | 7.1836 | 7.656 | 8.1283 | 7.656 | 5.7665 | 4.3494 | 3.877 | 2.9323 | 2.4599 | 1.9875 | 1.9875 | 1.5152 | 1.0428 | 1.9875 | 2.9323 | 3.4046 | 3.877 | 4.3494 | 4.8217
8 | 33 | 0 | 0 | 0.51743 | 1.5523 | 3.1046 | 3.622 | 3.622 | 4.1394 | 4.1394 | 4.6568 | 5.1743 | 5.6917 | 5.6917 | 6.2091 | 6.7265 | 6.2091 | 5.6917 | 5.1743 | 4.1394 | 3.1046 | 2.5871 | 2.5871 | 2.0697 | 2.0697 | 8 | 33 | 5.4367 | 4.9837 | 4.0775 | 3.6245 | 4.5306 | 5.8898 | 6.3428 | 6.7959 | 6.3428 | 4.5306 | 3.1714 | 2.7184 | 1.8122 | 1.3592 | 0.90612 | 0.90612 | 0.45306 | 0 | 0.90612 | 1.8122 | 2.2653 | 2.7184 | 3.1714 | 3.6245
8 | 34 | 0.69624 | 0.69624 | 1.2251 | 2.2828 | 3.8693 | 4.3981 | 4.3981 | 4.927 | 4.927 | 5.4558 | 5.9846 | 6.5135 | 6.5135 | 7.0423 | 7.5711 | 7.0423 | 6.5135 | 5.9846 | 4.927 | 3.8693 | 3.3404 | 3.3404 | 2.8116 | 2.8116 | 8 | 34 | 7.275 | 6.794 | 5.8322 | 5.3513 | 6.3131 | 7.7559 | 8.2368 | 8.7177 | 8.2368 | 6.3131 | 4.8704 | 4.3895 | 3.4277 | 2.9467 | 2.4658 | 2.4658 | 1.9849 | 1.504 | 2.4658 | 3.4277 | 3.9086 | 4.3895 | 4.8704 | 5.3513
8 | 35 | 1.3925 | 1.3925 | 1.9327 | 3.0132 | 4.634 | 5.1743 | 5.1743 | 5.7145 | 5.7145 | 6.2548 | 6.795 | 7.3353 | 7.3353 | 7.8755 | 8.4158 | 7.8755 | 7.3353 | 6.795 | 5.7145 | 4.634 | 4.0937 | 4.0937 | 3.5535 | 3.5535 | 8 | 35 | 9.1132 | 8.6044 | 7.5869 | 7.0781 | 8.0957 | 9.622 | 10.1307 | 10.6395 | 10.1307 | 8.0957 | 6.5694 | 6.0606 | 5.0431 | 4.5343 | 4.0255 | 4.0255 | 3.5168 | 3.008 | 4.0255 | 5.0431 | 5.5518 | 6.0606 | 6.5694 | 7.0781
9 | 36 | 5.9504 | 6.5021 | 5.9504 | 5.9504 | 5.9504 | 6.5021 | 7.0537 | 8.1571 | 8.7087 | 8.7087 | 9.2604 | 10.9154 | 11.4671 | 12.5704 | 13.1221 | 13.1221 | 12.5704 | 11.4671 | 10.9154 | 9.8121 | 8.7087 | 8.1571 | 8.1571 | 7.6054 | 9 | 36 | 17.3908 | 16.3176 | 15.781 | 15.781 | 16.3176 | 16.8542 | 17.3908 | 17.9274 | 18.4641 | 18.4641 | 17.3908 | 16.3176 | 15.781 | 15.2444 | 14.1711 | 13.6345 | 13.6345 | 14.1711 | 14.7077 | 15.781 | 16.3176 | 16.8542 | 16.3176 | 16.3176
9 | 37 | 6.7265 | 7.2896 | 6.7265 | 6.7265 | 6.7265 | 7.2896 | 7.8527 | 8.9788 | 9.5419 | 9.5419 | 10.105 | 11.7942 | 12.3573 | 13.4835 | 14.0466 | 14.0466 | 13.4835 | 12.3573 | 11.7942 | 10.6681 | 9.5419 | 8.9788 | 8.9788 | 8.4158 | 9 | 37 | 19.5633 | 18.4343 | 17.8699 | 17.8699 | 18.4343 | 18.9988 | 19.5633 | 20.1277 | 20.6922 | 20.6922 | 19.5633 | 18.4343 | 17.8699 | 17.3054 | 16.1765 | 15.612 | 15.612 | 16.1765 | 16.7409 | 17.8699 | 18.4343 | 18.9988 | 18.4343 | 18.4343
9 | 38 | 8.3823 | 8.9697 | 8.3823 | 8.3823 | 8.3823 | 8.9697 | 9.5571 | 10.732 | 11.3194 | 11.3194 | 11.9069 | 13.6692 | 14.2566 | 15.4314 | 16.0189 | 16.0189 | 15.4314 | 14.2566 | 13.6692 | 12.4943 | 11.3194 | 10.732 | 10.732 | 10.1446 | 9 | 38 | 21.4171 | 20.2406 | 19.6524 | 19.6524 | 20.2406 | 20.8289 | 21.4171 | 22.0053 | 22.5936 | 22.5936 | 21.4171 | 20.2406 | 19.6524 | 19.0642 | 17.8877 | 17.2995 | 17.2995 | 17.8877 | 18.4759 | 19.6524 | 20.2406 | 20.8289 | 20.2406 | 20.2406
9 | 39 | 10.038 | 10.6498 | 10.038 | 10.038 | 10.038 | 10.6498 | 11.2616 | 12.4852 | 13.0969 | 13.0969 | 13.7087 | 15.5441 | 16.1558 | 17.3794 | 17.9912 | 17.9912 | 17.3794 | 16.1558 | 15.5441 | 14.3205 | 13.0969 | 12.4852 | 12.4852 | 11.8734 | 9 | 39 | 23.2709 | 22.0469 | 21.4349 | 21.4349 | 22.0469 | 22.6589 | 23.2709 | 23.8829 | 24.4949 | 24.4949 | 23.2709 | 22.0469 | 21.4349 | 20.8229 | 19.5989 | 18.9869 | 18.9869 | 19.5989 | 20.2109 | 21.4349 | 22.0469 | 22.6589 | 22.0469 | 22.0469
10 | 40 | 20.5996 | 20.5996 | 20.5996 | 21.2357 | 21.8719 | 23.1441 | 23.7802 | 24.4164 | 25.6886 | 26.3248 | 26.9609 | 27.597 | 28.2331 | 28.2331 | 28.8693 | 28.8693 | 28.8693 | 28.8693 | 28.2331 | 27.597 | 27.597 | 27.597 | 27.597 | 26.3248 | 10 | 40 | 34.6613 | 33.3898 | 32.754 | 32.1182 | 32.1182 | 32.1182 | 32.754 | 33.3898 | 34.0255 | 33.3898 | 32.754 | 32.754 | 32.1182 | 31.4825 | 31.4825 | 31.4825 | 32.1182 | 33.3898 | 34.6613 | 36.5686 | 37.8402 | 37.8402 | 37.2044 | 35.9329
10 | 41 | 22.5963 | 22.5963 | 22.5963 | 23.2567 | 23.9172 | 25.2382 | 25.8986 | 26.5591 | 27.8801 | 28.5406 | 29.201 | 29.8615 | 30.522 | 30.522 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 30.522 | 29.8615 | 29.8615 | 29.8615 | 29.8615 | 28.5406 | 10 | 41 | 36.8717 | 35.5526 | 34.893 | 34.2335 | 34.2335 | 34.2335 | 34.893 | 35.5526 | 36.2121 | 35.5526 | 34.893 | 34.893 | 34.2335 | 33.574 | 33.574 | 33.574 | 34.2335 | 35.5526 | 36.8717 | 38.8503 | 40.1693 | 40.1693 | 39.5098 | 38.1907
10 | 42 | 24.5929 | 24.5929 | 24.5929 | 25.2777 | 25.9626 | 27.3322 | 28.017 | 28.7019 | 30.0715 | 30.7564 | 31.4412 | 32.126 | 32.8108 | 32.8108 | 33.4957 | 33.4957 | 33.4957 | 33.4957 | 32.8108 | 32.126 | 32.126 | 32.126 | 32.126 | 30.7564 | 10 | 42 | 39.082 | 37.7154 | 37.0321 | 36.3488 | 36.3488 | 36.3488 | 37.0321 | 37.7154 | 38.3987 | 37.7154 | 37.0321 | 37.0321 | 36.3488 | 35.6655 | 35.6655 | 35.6655 | 36.3488 | 37.7154 | 39.082 | 41.1319 | 42.4985 | 42.4985 | 41.8152 | 40.4486
10 | 43 | 26.6208 | 26.6208 | 26.6208 | 27.3303 | 28.0399 | 29.459 | 30.1685 | 30.8781 | 32.2972 | 33.0068 | 33.7163 | 34.4259 | 35.1354 | 35.1354 | 35.845 | 35.845 | 35.845 | 35.845 | 35.1354 | 34.4259 | 34.4259 | 34.4259 | 34.4259 | 33.0068 | 10 | 43 | 38.9093 | 37.5464 | 36.865 | 36.1835 | 36.1835 | 36.1835 | 36.865 | 37.5464 | 38.2279 | 37.5464 | 36.865 | 36.865 | 36.1835 | 35.5021 | 35.5021 | 35.5021 | 36.1835 | 37.5464 | 38.9093 | 40.9537 | 42.3165 | 42.3165 | 41.6351 | 40.2722
10 | 44 | 28.6486 | 28.6486 | 28.6486 | 29.3829 | 30.1172 | 31.5858 | 32.32 | 33.0543 | 34.5229 | 35.2572 | 35.9915 | 36.7258 | 37.4601 | 37.4601 | 38.1943 | 38.1943 | 38.1943 | 38.1943 | 37.4601 | 36.7258 | 36.7258 | 36.7258 | 36.7258 | 35.2572 | 10 | 44 | 38.7366 | 37.3775 | 36.6979 | 36.0183 | 36.0183 | 36.0183 | 36.6979 | 37.3775 | 38.057 | 37.3775 | 36.6979 | 36.6979 | 36.0183 | 35.3387 | 35.3387 | 35.3387 | 36.0183 | 37.3775 | 38.7366 | 40.7754 | 42.1346 | 42.1346 | 41.455 | 40.0958
11 | 45 | 42.8207 | 42.0617 | 42.0617 | 42.8207 | 42.8207 | 43.5797 | 45.0978 | 45.8568 | 47.3748 | 48.1338 | 49.6519 | 50.4109 | 49.6519 | 48.8929 | 47.3748 | 47.3748 | 46.6158 | 47.3748 | 47.3748 | 48.1338 | 48.8929 | 48.8929 | 49.6519 | 49.6519 | 11 | 45 | 35.853 | 34.4975 | 33.8198 | 33.8198 | 34.4975 | 35.1753 | 36.5307 | 37.2085 | 37.8862 | 37.8862 | 37.2085 | 37.2085 | 37.8862 | 37.8862 | 37.2085 | 36.5307 | 36.5307 | 36.5307 | 37.2085 | 37.8862 | 38.5639 | 39.2417 | 39.2417 | 38.5639
11 | 46 | 45.2443 | 44.4605 | 44.4605 | 45.2443 | 45.2443 | 46.028 | 47.5955 | 48.3792 | 49.9467 | 50.7305 | 52.298 | 53.0817 | 52.298 | 51.5142 | 49.9467 | 49.9467 | 49.163 | 49.9467 | 49.9467 | 50.7305 | 51.5142 | 51.5142 | 52.298 | 52.298 | 11 | 46 | 35.6878 | 34.336 | 33.6601 | 33.6601 | 34.336 | 35.0119 | 36.3636 | 37.0395 | 37.7154 | 37.7154 | 37.0395 | 37.0395 | 37.7154 | 37.7154 | 37.0395 | 36.3636 | 36.3636 | 36.3636 | 37.0395 | 37.7154 | 38.3913 | 39.0671 | 39.0671 | 38.3913
11 | 47 | 48.4135 | 47.5974 | 47.5974 | 48.4135 | 48.4135 | 49.2296 | 50.8617 | 51.6778 | 53.31 | 54.1261 | 55.7583 | 56.5743 | 55.7583 | 54.9422 | 53.31 | 53.31 | 52.4939 | 53.31 | 53.31 | 54.1261 | 54.9422 | 54.9422 | 55.7583 | 55.7583 | 11 | 47 | 36.6793 | 35.3053 | 34.6182 | 34.6182 | 35.3053 | 35.9923 | 37.3663 | 38.0533 | 38.7403 | 38.7403 | 38.0533 | 38.0533 | 38.7403 | 38.7403 | 38.0533 | 37.3663 | 37.3663 | 37.3663 | 38.0533 | 38.7403 | 39.4274 | 40.1144 | 40.1144 | 39.4274
11 | 48 | 51.5827 | 50.7343 | 50.7343 | 51.5827 | 51.5827 | 52.4311 | 54.128 | 54.9764 | 56.6733 | 57.5217 | 59.2185 | 60.067 | 59.2185 | 58.3701 | 56.6733 | 56.6733 | 55.8248 | 56.6733 | 56.6733 | 57.5217 | 58.3701 | 58.3701 | 59.2185 | 59.2185 | 11 | 48 | 37.6708 | 36.2745 | 35.5764 | 35.5764 | 36.2745 | 36.9727 | 38.369 | 39.0671 | 39.7653 | 39.7653 | 39.0671 | 39.0671 | 39.7653 | 39.7653 | 39.0671 | 38.369 | 38.369 | 38.369 | 39.0671 | 39.7653 | 40.4635 | 41.1616 | 41.1616 | 40.4635
12 | 49 | 69.7249 | 68.8442 | 68.8442 | 69.7249 | 69.7249 | 70.6057 | 72.3672 | 73.248 | 75.0095 | 76.771 | 77.6518 | 77.6518 | 76.771 | 75.8903 | 75.0095 | 74.1287 | 74.1287 | 74.1287 | 74.1287 | 75.0095 | 75.0095 | 75.8903 | 75.0095 | 74.1287 | 12 | 49 | 44.3367 | 43.6275 | 42.9182 | 42.9182 | 42.9182 | 43.6275 | 45.046 | 45.046 | 45.7553 | 45.046 | 44.3367 | 44.3367 | 44.3367 | 44.3367 | 43.6275 | 42.9182 | 42.2089 | 42.9182 | 44.3367 | 45.046 | 45.046 | 45.046 | 45.046 | 45.046
12 | 50 | 73.4439 | 72.5308 | 72.5308 | 73.4439 | 73.4439 | 74.357 | 76.1832 | 77.0963 | 78.9225 | 80.7487 | 81.6618 | 81.6618 | 80.7487 | 79.8356 | 78.9225 | 78.0094 | 78.0094 | 78.0094 | 78.0094 | 78.9225 | 78.9225 | 79.8356 | 78.9225 | 78.0094 | 12 | 50 | 45.4174 | 44.697 | 43.9765 | 43.9765 | 43.9765 | 44.697 | 46.1378 | 46.1378 | 46.8583 | 46.1378 | 45.4174 | 45.4174 | 45.4174 | 45.4174 | 44.697 | 43.9765 | 43.2561 | 43.9765 | 45.4174 | 46.1378 | 46.1378 | 46.1378 | 46.1378 | 46.1378
12 | 51 | 74.844 | 73.9187 | 73.9187 | 74.844 | 74.844 | 75.7693 | 77.6198 | 78.5451 | 80.3957 | 82.2462 | 83.1715 | 83.1715 | 82.2462 | 81.321 | 80.3957 | 79.4704 | 79.4704 | 79.4704 | 79.4704 | 80.3957 | 80.3957 | 81.321 | 80.3957 | 79.4704 | 12 | 51 | 47.2906 | 46.5508 | 45.8111 | 45.8111 | 45.8111 | 46.5508 | 48.0303 | 48.0303 | 48.7701 | 48.0303 | 47.2906 | 47.2906 | 47.2906 | 47.2906 | 46.5508 | 45.8111 | 45.0713 | 45.8111 | 47.2906 | 48.0303 | 48.0303 | 48.0303 | 48.0303 | 48.0303
12 | 52 | 76.2441 | 75.3067 | 75.3067 | 76.2441 | 76.2441 | 77.1816 | 79.0565 | 79.9939 | 81.8688 | 83.7437 | 84.6812 | 84.6812 | 83.7437 | 82.8063 | 81.8688 | 80.9314 | 80.9314 | 80.9314 | 80.9314 | 81.8688 | 81.8688 | 82.8063 | 81.8688 | 80.9314 | 12 | 52 | 49.1637 | 48.4046 | 47.6456 | 47.6456 | 47.6456 | 48.4046 | 49.9228 | 49.9228 | 50.6818 | 49.9228 | 49.1637 | 49.1637 | 49.1637 | 49.1637 | 48.4046 | 47.6456 | 46.8865 | 47.6456 | 49.1637 | 49.9228 | 49.9228 | 49.9228 | 49.9228 | 49.9228
WW |  | Hours | [23 empty] | WE |  | Hours
Month | Week | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Month | Week | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
1 | 1 | 82.1388 | 82.1388 | 82.7958 | 82.1388 | 82.1388 | 82.7958 | 84.1097 | 85.4237 | 86.7376 | 86.0806 | 84.1097 | 81.4818 | 79.5109 | 78.854 | 77.54 | 76.8831 | 76.2261 | 76.8831 | 79.5109 | 82.1388 | 84.1097 | 84.1097 | 83.4528 | 82.1388 | 1 | 1 | 62.4813 | 62.4813 | 63.418 | 64.3546 | 65.2913 | 66.2279 | 66.2279 | 66.2279 | 66.2279 | 64.3546 | 62.4813 | 61.5447 | 62.4813 | 62.4813 | 62.4813 | 61.5447 | 60.608 | 60.608 | 61.5447 | 63.418 | 64.3546 | 63.418 | 62.4813 | 61.5447
1 | 2 | 84.3411 | 84.3411 | 85.0137 | 84.3411 | 84.3411 | 85.0137 | 86.3588 | 87.704 | 89.0492 | 88.3766 | 86.3588 | 83.6685 | 81.6507 | 80.9781 | 79.633 | 78.9604 | 78.2878 | 78.9604 | 81.6507 | 84.3411 | 86.3588 | 86.3588 | 85.6863 | 84.3411 | 1 | 2 | 64.6077 | 64.6077 | 65.5637 | 66.5196 | 67.4756 | 68.4316 | 68.4316 | 68.4316 | 68.4316 | 66.5196 | 64.6077 | 63.6517 | 64.6077 | 64.6077 | 64.6077 | 63.6517 | 62.6957 | 62.6957 | 63.6517 | 65.5637 | 66.5196 | 65.5637 | 64.6077 | 63.6517
1 | 3 | 86.5433 | 86.5433 | 87.2316 | 86.5433 | 86.5433 | 87.2316 | 88.608 | 89.9844 | 91.3608 | 90.6726 | 88.608 | 85.8551 | 83.7905 | 83.1023 | 81.7259 | 81.0377 | 80.3495 | 81.0377 | 83.7905 | 86.5433 | 88.608 | 88.608 | 87.9198 | 86.5433 | 1 | 3 | 66.734 | 66.734 | 67.7093 | 68.6846 | 69.66 | 70.6353 | 70.6353 | 70.6353 | 70.6353 | 68.6846 | 66.734 | 65.7587 | 66.734 | 66.734 | 66.734 | 65.7587 | 64.7834 | 64.7834 | 65.7587 | 67.7093 | 68.6846 | 67.7093 | 66.734 | 65.7587
1 | 4 | 87.5757 | 87.5757 | 88.2712 | 87.5757 | 87.5757 | 88.2712 | 89.6622 | 91.0533 | 92.4444 | 91.7488 | 89.6622 | 86.8801 | 84.7935 | 84.098 | 82.707 | 82.0114 | 81.3159 | 82.0114 | 84.7935 | 87.5757 | 89.6622 | 89.6622 | 88.9667 | 87.5757 | 1 | 4 | 68.9087 | 68.9087 | 69.9038 | 70.8989 | 71.8939 | 72.889 | 72.889 | 72.889 | 72.889 | 70.8989 | 68.9087 | 67.9136 | 68.9087 | 68.9087 | 68.9087 | 67.9136 | 66.9185 | 66.9185 | 67.9136 | 69.9038 | 70.8989 | 69.9038 | 68.9087 | 67.9136
1 | 5 | 88.608 | 88.608 | 89.3108 | 88.608 | 88.608 | 89.3108 | 90.7165 | 92.1222 | 93.5279 | 92.8251 | 90.7165 | 87.9051 | 85.7966 | 85.0937 | 83.688 | 82.9852 | 82.2823 | 82.9852 | 85.7966 | 88.608 | 90.7165 | 90.7165 | 90.0137 | 88.608 | 1 | 5 | 71.0834 | 71.0834 | 72.0982 | 73.1131 | 74.1279 | 75.1428 | 75.1428 | 75.1428 | 75.1428 | 73.1131 | 71.0834 | 70.0685 | 71.0834 | 71.0834 | 71.0834 | 70.0685 | 69.0537 | 69.0537 | 70.0685 | 72.0982 | 73.1131 | 72.0982 | 71.0834 | 70.0685
2 | 6 | 91.0606 | 90.3504 | 91.0606 | 91.0606 | 91.7708 | 93.1911 | 94.6115 | 96.742 | 98.1623 | 98.8725 | 97.4522 | 94.6115 | 92.481 | 91.0606 | 90.3504 | 88.9301 | 88.9301 | 89.6403 | 91.7708 | 95.3217 | 97.4522 | 97.4522 | 96.742 | 96.0318 | 2 | 6 | 82.5696 | 82.5696 | 83.6043 | 85.6735 | 85.6735 | 86.7081 | 87.7427 | 88.7773 | 88.7773 | 85.6735 | 83.6043 | 82.5696 | 81.535 | 80.5004 | 80.5004 | 81.535 | 81.535 | 82.5696 | 83.6043 | 84.6389 | 84.6389 | 84.6389 | 84.6389 | 83.6043
2 | 7 | 92.1076 | 91.3901 | 92.1076 | 92.1076 | 92.8251 | 94.2601 | 95.695 | 97.8475 | 99.2825 | 100 | 98.565 | 95.695 | 93.5426 | 92.1076 | 91.3901 | 89.9551 | 89.9551 | 90.6726 | 92.8251 | 96.4125 | 98.565 | 98.565 | 97.8475 | 97.13 | 2 | 7 | 84.9222 | 84.9222 | 85.9766 | 88.0854 | 88.0854 | 89.1398 | 90.1942 | 91.2486 | 91.2486 | 88.0854 | 85.9766 | 84.9222 | 83.8678 | 82.8135 | 82.8135 | 83.8678 | 83.8678 | 84.9222 | 85.9766 | 87.031 | 87.031 | 87.031 | 87.031 | 85.9766
2 | 8 | 89.1412 | 88.4445 | 89.1412 | 89.1412 | 89.838 | 91.2315 | 92.625 | 94.7152 | 96.1087 | 96.8054 | 95.4119 | 92.625 | 90.5347 | 89.1412 | 88.4445 | 87.051 | 87.051 | 87.7477 | 89.838 | 93.3217 | 95.4119 | 95.4119 | 94.7152 | 94.0184 | 2 | 8 | 84.9222 | 84.9222 | 85.9766 | 88.0854 | 88.0854 | 89.1398 | 90.1942 | 91.2486 | 91.2486 | 88.0854 | 85.9766 | 84.9222 | 83.8678 | 82.8135 | 82.8135 | 83.8678 | 83.8678 | 84.9222 | 85.9766 | 87.031 | 87.031 | 87.031 | 87.031 | 85.9766
3 | 9 | 78.7388 | 78.0628 | 78.7388 | 78.7388 | 78.7388 | 78.0628 | 78.0628 | 78.7388 | 79.4148 | 79.4148 | 78.0628 | 75.3587 | 72.6547 | 71.9787 | 71.9787 | 71.9787 | 72.6547 | 74.0067 | 76.7108 | 79.4148 | 80.0908 | 80.7668 | 80.0908 | 78.7388 | 3 | 9 | 82.8135 | 82.8135 | 84.9222 | 85.9766 | 88.0854 | 89.1398 | 90.1942 | 89.1398 | 89.1398 | 87.031 | 85.9766 | 84.9222 | 82.8135 | 82.8135 | 83.8678 | 83.8678 | 83.8678 | 85.9766 | 85.9766 | 85.9766 | 85.9766 | 84.9222 | 83.8678 | 81.7591
3 | 10 | 76.0006 | 75.3453 | 76.0006 | 76.0006 | 76.0006 | 75.3453 | 75.3453 | 76.0006 | 76.6558 | 76.6558 | 75.3453 | 72.7243 | 70.1032 | 69.448 | 69.448 | 69.448 | 70.1032 | 71.4138 | 74.0348 | 76.6558 | 77.3111 | 77.9664 | 77.3111 | 76.0006 | 3 | 10 | 82.8135 | 82.8135 | 84.9222 | 85.9766 | 88.0854 | 89.1398 | 90.1942 | 89.1398 | 89.1398 | 87.031 | 85.9766 | 84.9222 | 82.8135 | 82.8135 | 83.8678 | 83.8678 | 83.8678 | 85.9766 | 85.9766 | 85.9766 | 85.9766 | 84.9222 | 83.8678 | 81.7591
3 | 11 | 73.2624 | 72.6279 | 73.2624 | 73.2624 | 73.2624 | 72.6279 | 72.6279 | 73.2624 | 73.8969 | 73.8969 | 72.6279 | 70.0898 | 67.5517 | 66.9172 | 66.9172 | 66.9172 | 67.5517 | 68.8208 | 71.3588 | 73.8969 | 74.5314 | 75.166 | 74.5314 | 73.2624 | 3 | 11 | 82.8135 | 82.8135 | 84.9222 | 85.9766 | 88.0854 | 89.1398 | 90.1942 | 89.1398 | 89.1398 | 87.031 | 85.9766 | 84.9222 | 82.8135 | 82.8135 | 83.8678 | 83.8678 | 83.8678 | 85.9766 | 85.9766 | 85.9766 | 85.9766 | 84.9222 | 83.8678 | 81.7591
3 | 12 | 71.0074 | 70.39 | 71.0074 | 71.0074 | 71.0074 | 70.39 | 70.39 | 71.0074 | 71.6249 | 71.6249 | 70.39 | 67.9202 | 65.4505 | 64.8331 | 64.8331 | 64.8331 | 65.4505 | 66.6854 | 69.1551 | 71.6249 | 72.2423 | 72.8597 | 72.2423 | 71.0074 | 3 | 12 | 83.8415 | 83.8415 | 85.9678 | 87.031 | 89.1574 | 90.2205 | 91.2837 | 90.2205 | 90.2205 | 88.0942 | 87.031 | 85.9678 | 83.8415 | 83.8415 | 84.9047 | 84.9047 | 84.9047 | 87.031 | 87.031 | 87.031 | 87.031 | 85.9678 | 84.9047 | 82.7783
3 | 13 | 68.7524 | 68.1521 | 68.7524 | 68.7524 | 68.7524 | 68.1521 | 68.1521 | 68.7524 | 69.3528 | 69.3528 | 68.1521 | 65.7507 | 63.3493 | 62.7489 | 62.7489 | 62.7489 | 63.3493 | 64.55 | 66.9514 | 69.3528 | 69.9531 | 70.5535 | 69.9531 | 68.7524 | 3 | 13 | 84.8695 | 84.8695 | 87.0134 | 88.0854 | 90.2293 | 91.3013 | 92.3733 | 91.3013 | 91.3013 | 89.1574 | 88.0854 | 87.0134 | 84.8695 | 84.8695 | 85.9415 | 85.9415 | 85.9415 | 88.0854 | 88.0854 | 88.0854 | 88.0854 | 87.0134 | 85.9415 | 83.7976
4 | 14 | 60.6648 | 60.0815 | 60.0815 | 60.0815 | 60.0815 | 60.0815 | 60.6648 | 61.248 | 61.248 | 58.915 | 54.8321 | 51.3325 | 48.4161 | 47.8329 | 47.8329 | 47.8329 | 49.5827 | 51.9158 | 55.4154 | 58.915 | 61.8313 | 62.9979 | 64.1644 | 62.9979 | 4 | 14 | 91.3013 | 91.3013 | 94.5435 | 97.7858 | 98.8665 | 97.7858 | 96.705 | 96.705 | 95.6243 | 92.382 | 90.2205 | 86.9783 | 84.8168 | 85.8975 | 88.059 | 90.2205 | 91.3013 | 93.4628 | 95.6243 | 96.705 | 96.705 | 97.7858 | 96.705 | 93.4628
4 | 15 | 58.5806 | 58.0144 | 58.0144 | 58.0144 | 58.0144 | 58.0144 | 58.5806 | 59.1468 | 59.1468 | 56.8821 | 52.9188 | 49.5217 | 46.6907 | 46.1246 | 46.1246 | 46.1246 | 47.8231 | 50.0879 | 53.485 | 56.8821 | 59.713 | 60.8454 | 61.9777 | 60.8454 | 4 | 15 | 92.3733 | 92.3733 | 95.6419 | 98.9105 | 100 | 98.9105 | 97.8209 | 97.8209 | 96.7314 | 93.4628 | 91.2837 | 88.0151 | 85.836 | 86.9256 | 89.1046 | 91.2837 | 92.3733 | 94.5523 | 96.7314 | 97.8209 | 97.8209 | 98.9105 | 97.8209 | 94.5523
4 | 16 | 57.747 | 57.1876 | 57.1876 | 57.1876 | 57.1876 | 57.1876 | 57.747 | 58.3063 | 58.3063 | 56.0689 | 52.1535 | 48.7973 | 46.0006 | 45.4412 | 45.4412 | 45.4412 | 47.1193 | 49.3567 | 52.7128 | 56.0689 | 58.8657 | 59.9844 | 61.1031 | 59.9844 | 4 | 16 | 92.1589 | 92.1589 | 95.4222 | 98.6855 | 99.7733 | 98.6855 | 97.5978 | 97.5978 | 96.51 | 93.2466 | 91.0711 | 87.8077 | 85.6322 | 86.72 | 88.8955 | 91.0711 | 92.1589 | 94.3344 | 96.51 | 97.5978 | 97.5978 | 98.6855 | 97.5978 | 94.3344
4 | 17 | 56.9133 | 56.3608 | 56.3608 | 56.3608 | 56.3608 | 56.3608 | 56.9133 | 57.4658 | 57.4658 | 55.2558 | 51.3881 | 48.073 | 45.3104 | 44.7579 | 44.7579 | 44.7579 | 46.4155 | 48.6255 | 51.9406 | 55.2558 | 58.0184 | 59.1234 | 60.2284 | 59.1234 | 4 | 17 | 91.9445 | 91.9445 | 95.2025 | 98.4606 | 99.5466 | 98.4606 | 97.3746 | 97.3746 | 96.2886 | 93.0305 | 90.8584 | 87.6004 | 85.4283 | 86.5144 | 88.6864 | 90.8584 | 91.9445 | 94.1165 | 96.2886 | 97.3746 | 97.3746 | 98.4606 | 97.3746 | 94.1165
5 | 18 | 52.8055 | 52.2599 | 52.2599 | 52.8055 | 52.8055 | 53.3512 | 53.8969 | 54.4426 | 54.9883 | 52.2599 | 47.8944 | 45.166 | 43.5289 | 42.9832 | 42.4375 | 41.3462 | 40.8005 | 42.4375 | 44.6203 | 48.4401 | 51.7142 | 51.7142 | 50.6228 | 48.9857 | 5 | 18 | 93.8986 | 93.8986 | 96.0671 | 98.2357 | 99.3199 | 99.3199 | 99.3199 | 99.3199 | 98.2357 | 94.9829 | 94.9829 | 91.7301 | 89.5615 | 87.393 | 87.393 | 88.4773 | 89.5615 | 89.5615 | 90.6458 | 91.7301 | 91.7301 | 91.7301 | 89.5615 | 87.393
5 | 19 | 52.0129 | 51.474 | 51.474 | 52.0129 | 52.0129 | 52.5517 | 53.0906 | 53.6294 | 54.1683 | 51.474 | 47.1632 | 44.469 | 42.8524 | 42.3135 | 41.7747 | 40.697 | 40.1581 | 41.7747 | 43.9301 | 47.7021 | 50.9352 | 50.9352 | 49.8575 | 48.2409 | 5 | 19 | 93.6807 | 93.6807 | 95.8457 | 98.0107 | 99.0932 | 99.0932 | 99.0932 | 99.0932 | 98.0107 | 94.7632 | 94.7632 | 91.5157 | 89.3507 | 87.1857 | 87.1857 | 88.2682 | 89.3507 | 89.3507 | 90.4332 | 91.5157 | 91.5157 | 91.5157 | 89.3507 | 87.1857
5 | 20 | 51.2202 | 50.6882 | 50.6882 | 51.2202 | 51.2202 | 51.7522 | 52.2843 | 52.8163 | 53.3483 | 50.6882 | 46.4321 | 43.772 | 42.1759 | 41.6439 | 41.1119 | 40.0478 | 39.5158 | 41.1119 | 43.2399 | 46.9641 | 50.1562 | 50.1562 | 49.0922 | 47.4961 | 5 | 20 | 93.4628 | 93.4628 | 95.6243 | 97.7858 | 98.8665 | 98.8665 | 98.8665 | 98.8665 | 97.7858 | 94.5435 | 94.5435 | 91.3013 | 89.1398 | 86.9783 | 86.9783 | 88.059 | 89.1398 | 89.1398 | 90.2205 | 91.3013 | 91.3013 | 91.3013 | 89.1398 | 86.9783
5 | 21 | 47.54 | 47.0397 | 47.0397 | 47.54 | 47.54 | 48.0403 | 48.5406 | 49.0409 | 49.5412 | 47.0397 | 43.0374 | 40.5359 | 39.035 | 38.5348 | 38.0345 | 37.0339 | 36.5336 | 38.0345 | 40.0356 | 43.5377 | 46.5394 | 46.5394 | 45.5389 | 44.038 | 5 | 21 | 89.1046 | 89.1046 | 91.1959 | 93.2871 | 94.3327 | 94.3327 | 94.3327 | 94.3327 | 93.2871 | 90.1503 | 90.1503 | 87.0134 | 84.9222 | 82.831 | 82.831 | 83.8766 | 84.9222 | 84.9222 | 85.9678 | 87.0134 | 87.0134 | 87.0134 | 84.9222 | 82.831
5 | 22 | 43.8598 | 43.3913 | 43.3913 | 43.8598 | 43.8598 | 44.3284 | 44.797 | 45.2655 | 45.7341 | 43.3913 | 39.6427 | 37.2999 | 35.8942 | 35.4256 | 34.957 | 34.0199 | 33.5513 | 34.957 | 36.8313 | 40.1113 | 42.9227 | 42.9227 | 41.9856 | 40.5799 | 5 | 22 | 84.7465 | 84.7465 | 86.7674 | 88.7883 | 89.7988 | 89.7988 | 89.7988 | 89.7988 | 88.7883 | 85.757 | 85.757 | 82.7256 | 80.7047 | 78.6838 | 78.6838 | 79.6942 | 80.7047 | 80.7047 | 81.7151 | 82.7256 | 82.7256 | 82.7256 | 80.7047 | 78.6838
6 | 23 | 30.1323 | 30.1323 | 30.1323 | 30.1323 | 30.5691 | 31.006 | 31.006 | 31.006 | 30.1323 | 26.2007 | 22.2691 | 20.0849 | 18.7744 | 18.7744 | 18.7744 | 18.7744 | 18.7744 | 19.6481 | 21.3955 | 23.5797 | 27.0744 | 28.3849 | 28.8217 | 28.3849 | 6 | 23 | 63.8081 | 63.8081 | 64.7834 | 65.7587 | 65.7587 | 66.734 | 66.734 | 66.734 | 63.8081 | 60.8822 | 59.9069 | 58.9316 | 58.9316 | 58.9316 | 59.9069 | 60.8822 | 62.8328 | 64.7834 | 65.7587 | 67.7093 | 67.7093 | 67.7093 | 65.7587 | 62.8328
6 | 24 | 27.1818 | 27.1818 | 27.1818 | 27.1818 | 27.5869 | 27.992 | 27.992 | 27.992 | 27.1818 | 23.5357 | 19.8897 | 17.8641 | 16.6488 | 16.6488 | 16.6488 | 16.6488 | 16.6488 | 17.459 | 19.0795 | 21.105 | 24.346 | 25.5613 | 25.9664 | 25.5613 | 6 | 24 | 60.0474 | 60.0474 | 60.9876 | 61.9278 | 61.9278 | 62.8679 | 62.8679 | 62.8679 | 60.0474 | 57.227 | 56.2868 | 55.3466 | 55.3466 | 55.3466 | 56.2868 | 57.227 | 59.1073 | 60.9876 | 61.9278 | 63.8081 | 63.8081 | 63.8081 | 61.9278 | 59.1073
6 | 25 | 23.4369 | 23.4369 | 23.4369 | 23.4369 | 23.8017 | 24.1666 | 24.1666 | 24.1666 | 23.4369 | 20.1533 | 16.8696 | 15.0454 | 13.9508 | 13.9508 | 13.9508 | 13.9508 | 13.9508 | 14.6805 | 16.1399 | 17.9642 | 20.883 | 21.9775 | 22.3423 | 21.9775 | 6 | 25 | 53.4663 | 53.4663 | 54.345 | 55.2236 | 55.2236 | 56.1023 | 56.1023 | 56.1023 | 53.4663 | 50.8303 | 49.9517 | 49.073 | 49.073 | 49.073 | 49.9517 | 50.8303 | 52.5876 | 54.345 | 55.2236 | 56.9809 | 56.9809 | 56.9809 | 55.2236 | 52.5876
6 | 26 | 19.692 | 19.692 | 19.692 | 19.692 | 20.0166 | 20.3412 | 20.3412 | 20.3412 | 19.692 | 16.7708 | 13.8496 | 12.2267 | 11.2529 | 11.2529 | 11.2529 | 11.2529 | 11.2529 | 11.9021 | 13.2004 | 14.8233 | 17.42 | 18.3937 | 18.7183 | 18.3937 | 6 | 26 | 46.8852 | 46.8852 | 47.7023 | 48.5195 | 48.5195 | 49.3366 | 49.3366 | 49.3366 | 46.8852 | 44.4337 | 43.6166 | 42.7994 | 42.7994 | 42.7994 | 43.6166 | 44.4337 | 46.068 | 47.7023 | 48.5195 | 50.1538 | 50.1538 | 50.1538 | 48.5195 | 46.068
7 | 27 | 4.2903 | 4.2903 | 4.006 | 4.006 | 4.006 | 4.5746 | 4.8589 | 5.1433 | 5.1433 | 2.5844 | 1.7315 | 2.0158 | 2.5844 | 3.1531 | 3.4374 | 3.4374 | 3.4374 | 3.1531 | 2.5844 | 2.3001 | 3.1531 | 3.7217 | 4.5746 | 4.8589 | 7 | 27 | 14.6121 | 14.6121 | 14.6121 | 15.3677 | 16.1234 | 16.879 | 18.3903 | 19.1459 | 19.1459 | 16.879 | 18.3903 | 19.9016 | 21.4129 | 22.1685 | 22.9242 | 22.9242 | 22.1685 | 22.1685 | 22.9242 | 22.9242 | 22.9242 | 21.4129 | 19.9016 | 17.6347
7 | 28 | 2.1964 | 2.1964 | 1.9524 | 1.9524 | 1.9524 | 2.4405 | 2.6845 | 2.9285 | 2.9285 | 0.73214 | 0 | 0.24405 | 0.73214 | 1.2202 | 1.4643 | 1.4643 | 1.4643 | 1.2202 | 0.73214 | 0.48809 | 1.2202 | 1.7083 | 2.4405 | 2.6845 | 7 | 28 | 10.1221 | 10.1221 | 10.1221 | 10.8163 | 11.5104 | 12.2046 | 13.5928 | 14.287 | 14.287 | 12.2046 | 13.5928 | 14.9811 | 16.3694 | 17.0635 | 17.7577 | 17.7577 | 17.0635 | 17.0635 | 17.7577 | 17.7577 | 17.7577 | 16.3694 | 14.9811 | 12.8987
7 | 29 | 2.3995 | 2.3995 | 2.1515 | 2.1515 | 2.1515 | 2.6474 | 2.8954 | 3.1433 | 3.1433 | 0.91175 | 0.1679 | 0.41585 | 0.91175 | 1.4077 | 1.6556 | 1.6556 | 1.6556 | 1.4077 | 0.91175 | 0.6638 | 1.4077 | 1.9036 | 2.6474 | 2.8954 | 7 | 29 | 9.2241 | 9.2241 | 9.2241 | 9.906 | 10.5878 | 11.2697 | 12.6333 | 13.3152 | 13.3152 | 11.2697 | 12.6333 | 13.997 | 15.3607 | 16.0425 | 16.7244 | 16.7244 | 16.0425 | 16.0425 | 16.7244 | 16.7244 | 16.7244 | 15.3607 | 13.997 | 11.9515
7 | 30 | 2.6025 | 2.6025 | 2.3506 | 2.3506 | 2.3506 | 2.8544 | 3.1062 | 3.3581 | 3.3581 | 1.0914 | 0.33581 | 0.58766 | 1.0914 | 1.5951 | 1.8469 | 1.8469 | 1.8469 | 1.5951 | 1.0914 | 0.83952 | 1.5951 | 2.0988 | 2.8544 | 3.1062 | 7 | 30 | 8.3262 | 8.3262 | 8.3262 | 8.9957 | 9.6652 | 10.3348 | 11.6738 | 12.3434 | 12.3434 | 10.3348 | 11.6738 | 13.0129 | 14.352 | 15.0215 | 15.6911 | 15.6911 | 15.0215 | 15.0215 | 15.6911 | 15.6911 | 15.6911 | 14.352 | 13.0129 | 11.0043
8 | 31 | 4.0843 | 3.8286 | 4.3401 | 4.5959 | 4.8516 | 4.8516 | 5.1074 | 5.3631 | 5.3631 | 3.3171 | 2.294 | 1.7825 | 1.7825 | 2.0383 | 2.5498 | 2.5498 | 2.8055 | 2.8055 | 2.294 | 1.7825 | 1.7825 | 2.0383 | 2.5498 | 2.5498 | 8 | 31 | 6.7709 | 6.7709 | 5.4565 | 6.1137 | 6.7709 | 6.7709 | 7.4282 | 8.0854 | 8.0854 | 6.1137 | 6.7709 | 8.0854 | 8.7426 | 8.7426 | 9.3999 | 8.0854 | 7.4282 | 8.0854 | 7.4282 | 6.1137 | 5.4565 | 4.7992 | 4.7992 | 4.7992
8 | 32 | 4.3069 | 4.0472 | 4.5666 | 4.8262 | 5.0859 | 5.0859 | 5.3456 | 5.6052 | 5.6052 | 3.5279 | 2.4893 | 1.9699 | 1.9699 | 2.2296 | 2.7489 | 2.7489 | 3.0086 | 3.0086 | 2.4893 | 1.9699 | 1.9699 | 2.2296 | 2.7489 | 2.7489 | 8 | 32 | 5.8852 | 5.8852 | 4.5954 | 5.2403 | 5.8852 | 5.8852 | 6.5302 | 7.1751 | 7.1751 | 5.2403 | 5.8852 | 7.1751 | 7.8201 | 7.8201 | 8.465 | 7.1751 | 6.5302 | 7.1751 | 6.5302 | 5.2403 | 4.5954 | 3.9504 | 3.9504 | 3.9504
8 | 33 | 4.5295 | 4.2659 | 4.793 | 5.0566 | 5.3202 | 5.3202 | 5.5838 | 5.8473 | 5.8473 | 3.7388 | 2.6845 | 2.1574 | 2.1574 | 2.4209 | 2.9481 | 2.9481 | 3.2116 | 3.2116 | 2.6845 | 2.1574 | 2.1574 | 2.4209 | 2.9481 | 2.9481 | 8 | 33 | 4.9996 | 4.9996 | 3.7343 | 4.3669 | 4.9996 | 4.9996 | 5.6322 | 6.2648 | 6.2648 | 4.3669 | 4.9996 | 6.2648 | 6.8975 | 6.8975 | 7.5301 | 6.2648 | 5.6322 | 6.2648 | 5.6322 | 4.3669 | 3.7343 | 3.1017 | 3.1017 | 3.1017
8 | 34 | 4.8772 | 4.6076 | 5.1469 | 5.4166 | 5.6863 | 5.6863 | 5.9559 | 6.2256 | 6.2256 | 4.0682 | 2.9896 | 2.4502 | 2.4502 | 2.7199 | 3.2592 | 3.2592 | 3.5289 | 3.5289 | 2.9896 | 2.4502 | 2.4502 | 2.7199 | 3.2592 | 3.2592 | 8 | 34 | 4.8414 | 4.8414 | 3.5805 | 4.211 | 4.8414 | 4.8414 | 5.4718 | 6.1023 | 6.1023 | 4.211 | 4.8414 | 6.1023 | 6.7327 | 6.7327 | 7.3631 | 6.1023 | 5.4718 | 6.1023 | 5.4718 | 4.211 | 3.5805 | 2.9501 | 2.9501 | 2.9501
8 | 35 | 5.225 | 4.9492 | 5.5008 | 5.7766 | 6.0523 | 6.0523 | 6.3281 | 6.6039 | 6.6039 | 4.3977 | 3.2946 | 2.7431 | 2.7431 | 3.0188 | 3.5704 | 3.5704 | 3.8462 | 3.8462 | 3.2946 | 2.7431 | 2.7431 | 3.0188 | 3.5704 | 3.5704 | 8 | 35 | 4.6832 | 4.6832 | 3.4268 | 4.055 | 4.6832 | 4.6832 | 5.3115 | 5.9397 | 5.9397 | 4.055 | 4.6832 | 5.9397 | 6.568 | 6.568 | 7.1962 | 5.9397 | 5.3115 | 5.9397 | 5.3115 | 4.055 | 3.4268 | 2.7985 | 2.7985 | 2.7985
9 | 36 | 6.9821 | 6.9821 | 7.264 | 7.5459 | 7.8278 | 8.1096 | 8.3915 | 8.3915 | 8.6734 | 5.8546 | 4.1634 | 3.8815 | 4.1634 | 4.4453 | 4.7272 | 4.4453 | 4.1634 | 3.8815 | 3.8815 | 4.4453 | 5.8546 | 6.4184 | 6.7003 | 6.7003 | 9 | 36 | 1.3949 | 2.0209 | 2.0209 | 2.0209 | 2.647 | 3.899 | 4.5251 | 4.5251 | 4.5251 | 2.647 | 3.273 | 3.899 | 4.5251 | 5.7772 | 7.0293 | 7.6553 | 6.4032 | 5.1511 | 4.5251 | 3.273 | 2.0209 | 2.0209 | 2.0209 | 0.14278
9 | 37 | 7.3604 | 7.3604 | 7.6484 | 7.9364 | 8.2243 | 8.5123 | 8.8003 | 8.8003 | 9.0882 | 6.2085 | 4.4807 | 4.1927 | 4.4807 | 4.7686 | 5.0566 | 4.7686 | 4.4807 | 4.1927 | 4.1927 | 4.7686 | 6.2085 | 6.7845 | 7.0724 | 7.0724 | 9 | 37 | 1.2477 | 1.8715 | 1.8715 | 1.8715 | 2.4954 | 3.7431 | 4.3669 | 4.3669 | 4.3669 | 2.4954 | 3.1192 | 3.7431 | 4.3669 | 5.6146 | 6.8623 | 7.4862 | 6.2385 | 4.9908 | 4.3669 | 3.1192 | 1.8715 | 1.8715 | 1.8715 | 0
9 | 38 | 8.8735 | 8.8735 | 9.1859 | 9.4982 | 9.8106 | 10.123 | 10.4354 | 10.4354 | 10.7478 | 7.624 | 5.7497 | 5.4373 | 5.7497 | 6.0621 | 6.3745 | 6.0621 | 5.7497 | 5.4373 | 5.4373 | 6.0621 | 7.624 | 8.2487 | 8.5611 | 8.5611 | 9 | 38 | 2.6606 | 3.3055 | 3.3055 | 3.3055 | 3.9504 | 5.2403 | 5.8852 | 5.8852 | 5.8852 | 3.9504 | 4.5954 | 5.2403 | 5.8852 | 7.1751 | 8.465 | 9.1099 | 7.8201 | 6.5302 | 5.8852 | 4.5954 | 3.3055 | 3.3055 | 3.3055 | 1.3707
9 | 39 | 10.3866 | 10.3866 | 10.7234 | 11.0601 | 11.3969 | 11.7337 | 12.0705 | 12.0705 | 12.4073 | 9.0394 | 7.0187 | 6.682 | 7.0187 | 7.3555 | 7.6923 | 7.3555 | 7.0187 | 6.682 | 6.682 | 7.3555 | 9.0394 | 9.713 | 10.0498 | 10.0498 | 9 | 39 | 4.0735 | 4.7395 | 4.7395 | 4.7395 | 5.4055 | 6.7375 | 7.4036 | 7.4036 | 7.4036 | 5.4055 | 6.0715 | 6.7375 | 7.4036 | 8.7356 | 10.0677 | 10.7337 | 9.4016 | 8.0696 | 7.4036 | 6.0715 | 4.7395 | 4.7395 | 4.7395 | 2.7414
10 | 40 | 19.8458 | 20.207 | 20.207 | 20.207 | 20.5681 | 21.2905 | 22.3741 | 23.4576 | 23.8188 | 22.0129 | 18.7622 | 17.3175 | 15.8727 | 15.1503 | 15.5115 | 15.8727 | 16.9563 | 17.6786 | 19.1234 | 20.9293 | 22.3741 | 22.7353 | 22.3741 | 21.6517 | 10 | 40 | 12.3574 | 13.7317 | 14.4188 | 15.1059 | 16.4801 | 17.8543 | 19.2285 | 18.5414 | 19.2285 | 16.4801 | 16.4801 | 16.4801 | 15.793 | 15.793 | 16.4801 | 18.5414 | 19.2285 | 19.9156 | 19.2285 | 17.1672 | 15.793 | 15.1059 | 14.4188 | 13.7317
10 | 41 | 21.8957 | 22.2813 | 22.2813 | 22.2813 | 22.6669 | 23.4381 | 24.5949 | 25.7517 | 26.1373 | 24.2093 | 20.739 | 19.1966 | 17.6542 | 16.8831 | 17.2686 | 17.6542 | 18.811 | 19.5822 | 21.1246 | 23.0525 | 24.5949 | 24.9805 | 24.5949 | 23.8237 | 10 | 41 | 13.9812 | 15.3976 | 16.1058 | 16.814 | 18.2304 | 19.6468 | 21.0632 | 20.355 | 21.0632 | 18.2304 | 18.2304 | 18.2304 | 17.5222 | 17.5222 | 18.2304 | 20.355 | 21.0632 | 21.7714 | 21.0632 | 18.9386 | 17.5222 | 16.814 | 16.1058 | 15.3976
10 | 42 | 23.9457 | 24.3557 | 24.3557 | 24.3557 | 24.7657 | 25.5857 | 26.8157 | 28.0457 | 28.4557 | 26.4057 | 22.7157 | 21.0758 | 19.4358 | 18.6158 | 19.0258 | 19.4358 | 20.6658 | 21.4857 | 23.1257 | 25.1757 | 26.8157 | 27.2257 | 26.8157 | 25.9957 | 10 | 42 | 15.605 | 17.0635 | 17.7928 | 18.5221 | 19.9807 | 21.4392 | 22.8978 | 22.1685 | 22.8978 | 19.9807 | 19.9807 | 19.9807 | 19.2514 | 19.2514 | 19.9807 | 22.1685 | 22.8978 | 23.6271 | 22.8978 | 20.71 | 19.2514 | 18.5221 | 17.7928 | 17.0635
10 | 43 | 26.5082 | 26.9487 | 26.9487 | 26.9487 | 27.3892 | 28.2702 | 29.5917 | 30.9132 | 31.3537 | 29.1512 | 25.1867 | 23.4247 | 21.6627 | 20.7817 | 21.2222 | 21.6627 | 22.9842 | 23.8652 | 25.6272 | 27.8297 | 29.5917 | 30.0322 | 29.5917 | 28.7107 | 10 | 43 | 16.9581 | 18.4518 | 19.1987 | 19.9455 | 21.4392 | 22.933 | 24.4267 | 23.6798 | 24.4267 | 21.4392 | 21.4392 | 21.4392 | 20.6924 | 20.6924 | 21.4392 | 23.6798 | 24.4267 | 25.1735 | 24.4267 | 22.1861 | 20.6924 | 19.9455 | 19.1987 | 18.4518
10 | 44 | 29.0707 | 29.5417 | 29.5417 | 29.5417 | 30.0127 | 30.9547 | 32.3677 | 33.7807 | 34.2518 | 31.8967 | 27.6577 | 25.7736 | 23.8896 | 22.9476 | 23.4186 | 23.8896 | 25.3026 | 26.2446 | 28.1287 | 30.4837 | 32.3677 | 32.8387 | 32.3677 | 31.4257 | 10 | 44 | 18.3112 | 19.8401 | 20.6045 | 21.3689 | 22.8978 | 24.4267 | 25.9555 | 25.1911 | 25.9555 | 22.8978 | 22.8978 | 22.8978 | 22.1334 | 22.1334 | 22.8978 | 25.1911 | 25.9555 | 26.72 | 25.9555 | 23.6622 | 22.1334 | 21.3689 | 20.6045 | 19.8401
11 | 45 | 44.171 | 43.6695 | 43.6695 | 43.168 | 43.168 | 44.171 | 45.174 | 46.6785 | 47.6816 | 47.6816 | 45.6755 | 43.168 | 40.6604 | 39.1558 | 38.1528 | 38.6543 | 39.1558 | 40.6604 | 43.6695 | 46.177 | 47.6816 | 48.1831 | 48.6846 | 47.6816 | 11 | 45 | 25.9204 | 25.1384 | 25.9204 | 27.4844 | 29.8304 | 31.3944 | 32.9584 | 34.5224 | 34.5224 | 33.7404 | 32.1764 | 31.3944 | 31.3944 | 31.3944 | 30.6124 | 30.6124 | 31.3944 | 31.3944 | 32.1764 | 32.1764 | 32.1764 | 32.1764 | 31.3944 | 30.6124
11 | 46 | 47.4961 | 46.9641 | 46.9641 | 46.4321 | 46.4321 | 47.4961 | 48.5601 | 50.1562 | 51.2202 | 51.2202 | 49.0922 | 46.4321 | 43.772 | 42.1759 | 41.1119 | 41.6439 | 42.1759 | 43.772 | 46.9641 | 49.6242 | 51.2202 | 51.7522 | 52.2843 | 51.2202 | 11 | 46 | 27.4141 | 26.6145 | 27.4141 | 29.0133 | 31.412 | 33.0112 | 34.6103 | 36.2095 | 36.2095 | 35.4099 | 33.8107 | 33.0112 | 33.0112 | 33.0112 | 32.2116 | 32.2116 | 33.0112 | 33.0112 | 33.8107 | 33.8107 | 33.8107 | 33.8107 | 33.0112 | 32.2116
11 | 47 | 49.6242 | 49.0726 | 49.0726 | 48.5211 | 48.5211 | 49.6242 | 50.7273 | 52.3819 | 53.485 | 53.485 | 51.2788 | 48.5211 | 45.7634 | 44.1087 | 43.0057 | 43.5572 | 44.1087 | 45.7634 | 49.0726 | 51.8303 | 53.485 | 54.0365 | 54.5881 | 53.485 | 11 | 47 | 29.0945 | 28.2752 | 29.0945 | 30.7332 | 33.1913 | 34.83 | 36.4687 | 38.1074 | 38.1074 | 37.288 | 35.6493 | 34.83 | 34.83 | 34.83 | 34.0106 | 34.0106 | 34.83 | 34.83 | 35.6493 | 35.6493 | 35.6493 | 35.6493 | 34.83 | 34.0106
11 | 48 | 51.7522 | 51.1812 | 51.1812 | 50.6101 | 50.6101 | 51.7522 | 52.8944 | 54.6076 | 55.7497 | 55.7497 | 53.4654 | 50.6101 | 47.7548 | 46.0416 | 44.8995 | 45.4705 | 46.0416 | 47.7548 | 51.1812 | 54.0365 | 55.7497 | 56.3208 | 56.8918 | 55.7497 | 11 | 48 | 30.775 | 29.9359 | 30.775 | 32.4532 | 34.9706 | 36.6488 | 38.327 | 40.0053 | 40.0053 | 39.1662 | 37.4879 | 36.6488 | 36.6488 | 36.6488 | 35.8097 | 35.8097 | 36.6488 | 36.6488 | 37.4879 | 37.4879 | 37.4879 | 37.4879 | 36.6488 | 35.8097
12 | 49 | 63.3298 | 62.7392 | 62.7392 | 62.7392 | 62.7392 | 63.3298 | 64.5109 | 65.6921 | 66.8733 | 67.4639 | 66.8733 | 63.9203 | 60.9674 | 58.605 | 57.4239 | 57.4239 | 59.1956 | 60.9674 | 63.3298 | 65.1015 | 65.6921 | 66.2827 | 65.6921 | 64.5109 | 12 | 49 | 39.3265 | 39.3265 | 41.0443 | 42.7621 | 44.4798 | 45.3387 | 47.0565 | 48.7743 | 47.9154 | 47.9154 | 46.1976 | 46.1976 | 45.3387 | 44.4798 | 44.4798 | 45.3387 | 45.3387 | 46.1976 | 46.1976 | 46.1976 | 46.1976 | 46.1976 | 45.3387 | 45.3387
12 | 50 | 65.7702 | 65.1601 | 65.1601 | 65.1601 | 65.1601 | 65.7702 | 66.9904 | 68.2107 | 69.4309 | 70.041 | 69.4309 | 66.3803 | 63.3298 | 60.8893 | 59.6691 | 59.6691 | 61.4994 | 63.3298 | 65.7702 | 67.6005 | 68.2107 | 68.8208 | 68.2107 | 66.9904 | 12 | 50 | 41.1651 | 41.1651 | 42.9224 | 44.6797 | 46.437 | 47.3157 | 49.073 | 50.8303 | 49.9517 | 49.9517 | 48.1944 | 48.1944 | 47.3157 | 46.437 | 46.437 | 47.3157 | 47.3157 | 48.1944 | 48.1944 | 48.1944 | 48.1944 | 48.1944 | 47.3157 | 47.3157
12 | 51 | 67.7226 | 67.0968 | 67.0968 | 67.0968 | 67.0968 | 67.7226 | 68.974 | 70.2255 | 71.477 | 72.1027 | 71.477 | 68.3483 | 65.2196 | 62.7167 | 61.4652 | 61.4652 | 63.3424 | 65.2196 | 67.7226 | 69.5998 | 70.2255 | 70.8512 | 70.2255 | 68.974 | 12 | 51 | 42.9628 | 42.9628 | 44.7588 | 46.5548 | 48.3508 | 49.2487 | 51.0447 | 52.8407 | 51.9427 | 51.9427 | 50.1467 | 50.1467 | 49.2487 | 48.3508 | 48.3508 | 49.2487 | 49.2487 | 50.1467 | 50.1467 | 50.1467 | 50.1467 | 50.1467 | 49.2487 | 49.2487
12 | 52 | 69.6749 | 69.0336 | 69.0336 | 69.0336 | 69.0336 | 69.6749 | 70.9576 | 72.2403 | 73.523 | 74.1644 | 73.523 | 70.3163 | 67.1095 | 64.5441 | 63.2614 | 63.2614 | 65.1855 | 67.1095 | 69.6749 | 71.599 | 72.2403 | 72.8817 | 72.2403 | 70.9576 | 12 | 52 | 44.7606 | 44.7606 | 46.5952 | 48.4298 | 50.2645 | 51.1818 | 53.0164 | 54.8511 | 53.9337 | 53.9337 | 52.0991 | 52.0991 | 51.1818 | 50.2645 | 50.2645 | 51.1818 | 51.1818 | 52.0991 | 52.0991 | 52.0991 | 52.0991 | 52.0991 | 51.1818 | 51.1818

## Equivalent Week Profile Wind
Month | Day | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Original
1 | 1 | 88.0901 | 89.0397 | 88.0901 | 88.0901 | 88.0901 | 89.0397 | 89.9893 | 90.939 | 92.8382 | 91.8886 | 90.939 | 90.939 | 89.9893 | 89.9893 | 89.0397 | 89.0397 | 88.0901 | 88.0901 | 88.0901 | 89.0397 | 89.9893 | 90.939 | 89.9893 | 88.0901 | 1
1 | 2 | 89.6241 | 90.5859 | 89.6241 | 89.6241 | 89.6241 | 90.5859 | 91.5477 | 92.5095 | 94.4331 | 93.4713 | 92.5095 | 92.5095 | 91.5477 | 91.5477 | 90.5859 | 90.5859 | 89.6241 | 89.6241 | 89.6241 | 90.5859 | 91.5477 | 92.5095 | 91.5477 | 89.6241 | 1
1 | 3 | 90.5253 | 91.4943 | 90.5253 | 90.5253 | 90.5253 | 91.4943 | 92.4632 | 93.4322 | 95.3701 | 94.4012 | 93.4322 | 93.4322 | 92.4632 | 92.4632 | 91.4943 | 91.4943 | 90.5253 | 90.5253 | 90.5253 | 91.4943 | 92.4632 | 93.4322 | 92.4632 | 90.5253
1 | 4 | 91.1581 | 92.1321 | 91.1581 | 91.1581 | 91.1581 | 92.1321 | 93.1061 | 94.08 | 96.028 | 95.054 | 94.08 | 94.08 | 93.1061 | 93.1061 | 92.1321 | 92.1321 | 91.1581 | 91.1581 | 91.1581 | 92.1321 | 93.1061 | 94.08 | 93.1061 | 91.1581 | 1
1 | 5 | 75.4378 | 76.2452 | 75.4378 | 75.4378 | 75.4378 | 76.2452 | 77.0527 | 77.8602 | 79.4751 | 78.6676 | 77.8602 | 77.8602 | 77.0527 | 77.0527 | 76.2452 | 76.2452 | 75.4378 | 75.4378 | 75.4378 | 76.2452 | 77.0527 | 77.8602 | 77.0527 | 75.4378
1 | 6 | 91.6375 | 92.6153 | 91.6375 | 91.6375 | 91.6375 | 92.6153 | 93.5931 | 94.5708 | 96.5264 | 95.5486 | 94.5708 | 94.5708 | 93.5931 | 93.5931 | 92.6153 | 92.6153 | 91.6375 | 91.6375 | 91.6375 | 92.6153 | 93.5931 | 94.5708 | 93.5931 | 91.6375 | 1
1 | 7 | 92.1169 | 93.0985 | 92.1169 | 92.1169 | 92.1169 | 93.0985 | 94.08 | 95.0616 | 97.0248 | 96.0432 | 95.0616 | 95.0616 | 94.08 | 94.08 | 93.0985 | 93.0985 | 92.1169 | 92.1169 | 92.1169 | 93.0985 | 94.08 | 95.0616 | 94.08 | 92.1169 | 1
2 | 8 | 91.7174 | 91.7174 | 92.6958 | 92.6958 | 91.7174 | 91.7174 | 93.6742 | 94.6526 | 95.6311 | 97.5879 | 98.5663 | 98.5663 | 97.5879 | 96.6095 | 96.6095 | 94.6526 | 94.6526 | 95.6311 | 96.6095 | 97.5879 | 97.5879 | 98.5663 | 97.5879 | 95.6311
2 | 9 | 92.5963 | 92.5963 | 93.5816 | 93.5816 | 92.5963 | 92.5963 | 94.567 | 95.5524 | 96.5378 | 98.5086 | 99.494 | 99.494 | 98.5086 | 97.5232 | 97.5232 | 95.5524 | 95.5524 | 96.5378 | 97.5232 | 98.5086 | 98.5086 | 99.494 | 98.5086 | 96.5378 | 2
2 | 10 | 91.7174 | 91.7174 | 92.6958 | 92.6958 | 91.7174 | 91.7174 | 93.6742 | 94.6526 | 95.6311 | 97.5879 | 98.5663 | 98.5663 | 97.5879 | 96.6095 | 96.6095 | 94.6526 | 94.6526 | 95.6311 | 96.6095 | 97.5879 | 97.5879 | 98.5663 | 97.5879 | 95.6311
2 | 11 | 93.0756 | 93.0756 | 94.0648 | 94.0648 | 93.0756 | 93.0756 | 95.054 | 96.0432 | 97.0324 | 99.0108 | 100 | 100 | 99.0108 | 98.0216 | 98.0216 | 96.0432 | 96.0432 | 97.0324 | 98.0216 | 99.0108 | 99.0108 | 100 | 99.0108 | 97.0324 | 2
2 | 12 | 91.7174 | 91.7174 | 92.6958 | 92.6958 | 91.7174 | 91.7174 | 93.6742 | 94.6526 | 95.6311 | 97.5879 | 98.5663 | 98.5663 | 97.5879 | 96.6095 | 96.6095 | 94.6526 | 94.6526 | 95.6311 | 96.6095 | 97.5879 | 97.5879 | 98.5663 | 97.5879 | 95.6311
2 | 13 | 89.4803 | 89.4803 | 90.441 | 90.441 | 89.4803 | 89.4803 | 91.4016 | 92.3623 | 93.3229 | 95.2443 | 96.2049 | 96.2049 | 95.2443 | 94.2836 | 94.2836 | 92.3623 | 92.3623 | 93.3229 | 94.2836 | 95.2443 | 95.2443 | 96.2049 | 95.2443 | 93.3229 | 2
2 | 14 | 67.3383 | 66.4553 | 66.4553 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 68.2214 | 69.1044 | 70.8705 | 71.7535 | 71.7535 | 70.8705 | 69.9874 | 69.9874 | 71.7535 | 71.7535 | 72.6366 | 71.7535 | 71.7535 | 72.6366 | 70.8705 | 70.8705 | 69.1044
3 | 15 | 72.8352 | 71.9031 | 71.9031 | 72.8352 | 72.8352 | 72.8352 | 72.8352 | 73.7673 | 74.6994 | 76.5637 | 77.4958 | 77.4958 | 76.5637 | 75.6316 | 75.6316 | 77.4958 | 77.4958 | 78.4279 | 77.4958 | 77.4958 | 78.4279 | 76.5637 | 76.5637 | 74.6994 | 3
3 | 16 | 69.6393 | 68.7357 | 68.7357 | 69.6393 | 69.6393 | 69.6393 | 69.6393 | 70.5429 | 71.4465 | 73.2537 | 74.1573 | 74.1573 | 73.2537 | 72.3501 | 72.3501 | 74.1573 | 74.1573 | 75.0609 | 74.1573 | 74.1573 | 75.0609 | 73.2537 | 73.2537 | 71.4465 | 3
3 | 17 | 67.3383 | 66.4553 | 66.4553 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 68.2214 | 69.1044 | 70.8705 | 71.7535 | 71.7535 | 70.8705 | 69.9874 | 69.9874 | 71.7535 | 71.7535 | 72.6366 | 71.7535 | 71.7535 | 72.6366 | 70.8705 | 70.8705 | 69.1044
3 | 18 | 66.4435 | 65.5684 | 65.5684 | 66.4435 | 66.4435 | 66.4435 | 66.4435 | 67.3185 | 68.1936 | 69.9437 | 70.8187 | 70.8187 | 69.9437 | 69.0686 | 69.0686 | 70.8187 | 70.8187 | 71.6938 | 70.8187 | 70.8187 | 71.6938 | 69.9437 | 69.9437 | 68.1936 | 3
3 | 19 | 67.3383 | 66.4553 | 66.4553 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 68.2214 | 69.1044 | 70.8705 | 71.7535 | 71.7535 | 70.8705 | 69.9874 | 69.9874 | 71.7535 | 71.7535 | 72.6366 | 71.7535 | 71.7535 | 72.6366 | 70.8705 | 70.8705 | 69.1044
3 | 20 | 64.739 | 63.8792 | 63.8792 | 64.739 | 64.739 | 64.739 | 64.739 | 65.5988 | 66.4587 | 68.1784 | 69.0382 | 69.0382 | 68.1784 | 67.3185 | 67.3185 | 69.0382 | 69.0382 | 69.898 | 69.0382 | 69.0382 | 69.898 | 68.1784 | 68.1784 | 66.4587 | 3
3 | 21 | 63.0345 | 62.1899 | 62.1899 | 63.0345 | 63.0345 | 63.0345 | 63.0345 | 63.8792 | 64.7238 | 66.413 | 67.2576 | 67.2576 | 66.413 | 65.5684 | 65.5684 | 67.2576 | 67.2576 | 68.1023 | 67.2576 | 67.2576 | 68.1023 | 66.413 | 66.413 | 64.7238 | 3
4 | 22 | 55.5243 | 53.8655 | 53.0361 | 53.0361 | 53.0361 | 53.0361 | 53.8655 | 54.6949 | 54.6949 | 55.5243 | 56.3537 | 56.3537 | 56.3537 | 56.3537 | 57.1831 | 58.0125 | 58.8419 | 59.6713 | 60.5007 | 61.3301 | 61.3301 | 62.1595 | 61.3301 | 59.6713 | 4
4 | 23 | 54.3258 | 52.6898 | 51.8719 | 51.8719 | 51.8719 | 51.8719 | 52.6898 | 53.5078 | 53.5078 | 54.3258 | 55.1438 | 55.1438 | 55.1438 | 55.1438 | 55.9618 | 56.7798 | 57.5978 | 58.4158 | 59.2338 | 60.0517 | 60.0517 | 60.8697 | 60.0517 | 58.4158
4 | 24 | 53.9263 | 52.298 | 51.4838 | 51.4838 | 51.4838 | 51.4838 | 52.298 | 53.1122 | 53.1122 | 53.9263 | 54.7405 | 54.7405 | 54.7405 | 54.7405 | 55.5547 | 56.3689 | 57.1831 | 57.9973 | 58.8114 | 59.6256 | 59.6256 | 60.4398 | 59.6256 | 57.9973 | 4
4 | 25 | 54.3258 | 52.6898 | 51.8719 | 51.8719 | 51.8719 | 51.8719 | 52.6898 | 53.5078 | 53.5078 | 54.3258 | 55.1438 | 55.1438 | 55.1438 | 55.1438 | 55.9618 | 56.7798 | 57.5978 | 58.4158 | 59.2338 | 60.0517 | 60.0517 | 60.8697 | 60.0517 | 58.4158
4 | 26 | 53.9263 | 52.298 | 51.4838 | 51.4838 | 51.4838 | 51.4838 | 52.298 | 53.1122 | 53.1122 | 53.9263 | 54.7405 | 54.7405 | 54.7405 | 54.7405 | 55.5547 | 56.3689 | 57.1831 | 57.9973 | 58.8114 | 59.6256 | 59.6256 | 60.4398 | 59.6256 | 57.9973 | 4
4 | 27 | 54.3258 | 52.6898 | 51.8719 | 51.8719 | 51.8719 | 51.8719 | 52.6898 | 53.5078 | 53.5078 | 54.3258 | 55.1438 | 55.1438 | 55.1438 | 55.1438 | 55.9618 | 56.7798 | 57.5978 | 58.4158 | 59.2338 | 60.0517 | 60.0517 | 60.8697 | 60.0517 | 58.4158
4 | 28 | 53.9263 | 52.298 | 51.4838 | 51.4838 | 51.4838 | 51.4838 | 52.298 | 53.1122 | 53.1122 | 53.9263 | 54.7405 | 54.7405 | 54.7405 | 54.7405 | 55.5547 | 56.3689 | 57.1831 | 57.9973 | 58.8114 | 59.6256 | 59.6256 | 60.4398 | 59.6256 | 57.9973 | 4
5 | 29 | 53.9263 | 52.298 | 51.4838 | 50.6696 | 50.6696 | 51.4838 | 52.298 | 53.1122 | 54.7405 | 54.7405 | 56.3689 | 56.3689 | 56.3689 | 57.1831 | 57.9973 | 59.6256 | 59.6256 | 60.4398 | 61.254 | 60.4398 | 59.6256 | 58.8114 | 57.1831 | 54.7405 | 5
5 | 30 | 53.9263 | 52.298 | 51.4838 | 50.6696 | 50.6696 | 51.4838 | 52.298 | 53.1122 | 54.7405 | 54.7405 | 56.3689 | 56.3689 | 56.3689 | 57.1831 | 57.9973 | 59.6256 | 59.6256 | 60.4398 | 61.254 | 60.4398 | 59.6256 | 58.8114 | 57.1831 | 54.7405 | 5
5 | 31 | 52.5282 | 50.9264 | 50.1256 | 49.4604 | 49.4604 | 50.1256 | 50.9264 | 51.7273 | 53.0576 | 53.1933 | 54.6594 | 54.6594 | 54.6594 | 55.3245 | 56.1254 | 57.5914 | 57.7271 | 58.528 | 59.3289 | 58.7994 | 58.1342 | 57.6048 | 56.1387 | 53.8718
5 | 32 | 53.9263 | 52.298 | 51.4838 | 50.6696 | 50.6696 | 51.4838 | 52.298 | 53.1122 | 54.7405 | 54.7405 | 56.3689 | 56.3689 | 56.3689 | 57.1831 | 57.9973 | 59.6256 | 59.6256 | 60.4398 | 61.254 | 60.4398 | 59.6256 | 58.8114 | 57.1831 | 54.7405 | 5
5 | 33 | 51.13 | 49.5549 | 48.7673 | 47.9798 | 47.9798 | 48.7673 | 49.5549 | 50.3424 | 51.9175 | 51.9175 | 53.4926 | 53.4926 | 53.4926 | 54.2802 | 55.0677 | 56.6428 | 56.6428 | 57.4304 | 58.2179 | 57.4304 | 56.6428 | 55.8553 | 54.2802 | 51.9175 | 5
5 | 34 | 52.5282 | 50.9264 | 50.1256 | 49.4604 | 49.4604 | 50.1256 | 50.9264 | 51.7273 | 53.0576 | 53.1933 | 54.6594 | 54.6594 | 54.6594 | 55.3245 | 56.1254 | 57.5914 | 57.7271 | 58.528 | 59.3289 | 58.7994 | 58.1342 | 57.6048 | 56.1387 | 53.8718
5 | 35 | 48.3336 | 46.8117 | 46.0508 | 45.2899 | 45.2899 | 46.0508 | 46.8117 | 47.5727 | 49.0945 | 49.0945 | 50.6163 | 50.6163 | 50.6163 | 51.3773 | 52.1382 | 53.66 | 53.66 | 54.4209 | 55.1819 | 54.4209 | 53.66 | 52.8991 | 51.3773 | 49.0945 | 5
6 | 36 | 36.7258 | 35.9915 | 34.5229 | 34.5229 | 33.7886 | 33.7886 | 34.5229 | 34.5229 | 35.2572 | 35.9915 | 36.7258 | 37.4601 | 36.7258 | 36.7258 | 37.4601 | 37.4601 | 37.4601 | 38.1943 | 39.6629 | 38.9286 | 38.1943 | 37.4601 | 36.7258 | 35.9915 | 6
6 | 37 | 31.6837 | 31.0037 | 29.6435 | 29.6435 | 28.9634 | 28.9634 | 29.6435 | 29.6435 | 30.3236 | 31.0037 | 31.6837 | 32.3638 | 31.6837 | 31.6837 | 32.3638 | 32.3638 | 32.3638 | 33.0439 | 34.404 | 33.7239 | 33.0439 | 32.3638 | 31.6837 | 31.0037
6 | 38 | 34.249 | 33.5413 | 32.126 | 32.126 | 31.4184 | 31.4184 | 32.126 | 32.126 | 32.8337 | 33.5413 | 34.249 | 34.9566 | 34.249 | 34.249 | 34.9566 | 34.9566 | 34.9566 | 35.6643 | 37.0796 | 36.3719 | 35.6643 | 34.9566 | 34.249 | 33.5413 | 6
6 | 39 | 31.6837 | 31.0037 | 29.6435 | 29.6435 | 28.9634 | 28.9634 | 29.6435 | 29.6435 | 30.3236 | 31.0037 | 31.6837 | 32.3638 | 31.6837 | 31.6837 | 32.3638 | 32.3638 | 32.3638 | 33.0439 | 34.404 | 33.7239 | 33.0439 | 32.3638 | 31.6837 | 31.0037
6 | 40 | 30.003 | 29.341 | 28.017 | 28.017 | 27.355 | 27.355 | 28.017 | 28.017 | 28.679 | 29.341 | 30.003 | 30.665 | 30.003 | 30.003 | 30.665 | 30.665 | 30.665 | 31.327 | 32.651 | 31.989 | 31.327 | 30.665 | 30.003 | 29.341 | 6
6 | 41 | 31.6837 | 31.0037 | 29.6435 | 29.6435 | 28.9634 | 28.9634 | 29.6435 | 29.6435 | 30.3236 | 31.0037 | 31.6837 | 32.3638 | 31.6837 | 31.6837 | 32.3638 | 32.3638 | 32.3638 | 33.0439 | 34.404 | 33.7239 | 33.0439 | 32.3638 | 31.6837 | 31.0037
6 | 42 | 25.7571 | 25.1408 | 23.9081 | 23.9081 | 23.2917 | 23.2917 | 23.9081 | 23.9081 | 24.5244 | 25.1408 | 25.7571 | 26.3735 | 25.7571 | 25.7571 | 26.3735 | 26.3735 | 26.3735 | 26.9898 | 28.2225 | 27.6061 | 26.9898 | 26.3735 | 25.7571 | 25.1408 | 6
7 | 43 | 5.5319 | 5.5319 | 5.5319 | 5.5319 | 5.5319 | 6.6733 | 6.6733 | 7.244 | 7.244 | 7.244 | 8.3853 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 9.5267 | 10.0974 | 8.956 | 8.3853 | 7.244 | 6.1026 | 5.5319 | 7
7 | 44 | 3.232 | 3.232 | 3.232 | 3.232 | 3.232 | 4.3026 | 4.3026 | 4.8379 | 4.8379 | 4.8379 | 5.9085 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 7.5145 | 6.4438 | 5.9085 | 4.8379 | 3.7673 | 3.232
7 | 45 | 2.5643 | 2.5643 | 2.5643 | 2.5643 | 2.5643 | 3.6144 | 3.6144 | 4.1394 | 4.1394 | 4.1394 | 5.1895 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.2395 | 6.7646 | 5.7145 | 5.1895 | 4.1394 | 3.0893 | 2.5643 | 7
7 | 46 | 3.232 | 3.232 | 3.232 | 3.232 | 3.232 | 4.3026 | 4.3026 | 4.8379 | 4.8379 | 4.8379 | 5.9085 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 7.5145 | 6.4438 | 5.9085 | 4.8379 | 3.7673 | 3.232
7 | 47 | 2.4654 | 2.4654 | 2.4654 | 2.4654 | 2.4654 | 3.5124 | 3.5124 | 4.0359 | 4.0359 | 4.0359 | 5.0829 | 6.13 | 6.13 | 6.13 | 6.13 | 6.13 | 6.13 | 6.13 | 6.6535 | 5.6065 | 5.0829 | 4.0359 | 2.9889 | 2.4654 | 7
7 | 48 | 3.232 | 3.232 | 3.232 | 3.232 | 3.232 | 4.3026 | 4.3026 | 4.8379 | 4.8379 | 4.8379 | 5.9085 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 6.9792 | 7.5145 | 6.4438 | 5.9085 | 4.8379 | 3.7673 | 3.232
7 | 49 | 2.3665 | 2.3665 | 2.3665 | 2.3665 | 2.3665 | 3.4104 | 3.4104 | 3.9324 | 3.9324 | 3.9324 | 4.9764 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.0204 | 6.5424 | 5.4984 | 4.9764 | 3.9324 | 2.8884 | 2.3665 | 7
8 | 50 | 0.18566 | 0.18566 | 0.70613 | 1.7471 | 3.3085 | 3.8289 | 3.8289 | 4.3494 | 4.3494 | 4.8699 | 5.3904 | 5.9108 | 5.9108 | 6.4313 | 6.9518 | 6.4313 | 5.9108 | 5.3904 | 4.3494 | 3.3085 | 2.788 | 2.788 | 2.2675 | 2.2675 | 8
8 | 51 | 0.092832 | 0.092832 | 0.61178 | 1.6497 | 3.2065 | 3.7255 | 3.7255 | 4.2444 | 4.2444 | 4.7634 | 5.2823 | 5.8012 | 5.8012 | 6.3202 | 6.8391 | 6.3202 | 5.8012 | 5.2823 | 4.2444 | 3.2065 | 2.6876 | 2.6876 | 2.1686 | 2.1686 | 8
8 | 52 | 0.39454 | 0.39454 | 0.83219 | 1.7075 | 3.0205 | 3.4581 | 3.4581 | 3.8958 | 3.8958 | 4.3334 | 4.7711 | 5.2087 | 5.2087 | 5.6464 | 6.0841 | 5.6464 | 5.2087 | 4.7711 | 3.8958 | 3.0205 | 2.5828 | 2.5828 | 2.1452 | 2.1452
8 | 53 | 0 | 0 | 0.51743 | 1.5523 | 3.1046 | 3.622 | 3.622 | 4.1394 | 4.1394 | 4.6568 | 5.1743 | 5.6917 | 5.6917 | 6.2091 | 6.7265 | 6.2091 | 5.6917 | 5.1743 | 4.1394 | 3.1046 | 2.5871 | 2.5871 | 2.0697 | 2.0697 | 8
8 | 54 | 0.39454 | 0.39454 | 0.83219 | 1.7075 | 3.0205 | 3.4581 | 3.4581 | 3.8958 | 3.8958 | 4.3334 | 4.7711 | 5.2087 | 5.2087 | 5.6464 | 6.0841 | 5.6464 | 5.2087 | 4.7711 | 3.8958 | 3.0205 | 2.5828 | 2.5828 | 2.1452 | 2.1452
8 | 55 | 0.69624 | 0.69624 | 1.2251 | 2.2828 | 3.8693 | 4.3981 | 4.3981 | 4.927 | 4.927 | 5.4558 | 5.9846 | 6.5135 | 6.5135 | 7.0423 | 7.5711 | 7.0423 | 6.5135 | 5.9846 | 4.927 | 3.8693 | 3.3404 | 3.3404 | 2.8116 | 2.8116 | 8
8 | 56 | 1.3925 | 1.3925 | 1.9327 | 3.0132 | 4.634 | 5.1743 | 5.1743 | 5.7145 | 5.7145 | 6.2548 | 6.795 | 7.3353 | 7.3353 | 7.8755 | 8.4158 | 7.8755 | 7.3353 | 6.795 | 5.7145 | 4.634 | 4.0937 | 4.0937 | 3.5535 | 3.5535 | 8
9 | 57 | 5.9504 | 6.5021 | 5.9504 | 5.9504 | 5.9504 | 6.5021 | 7.0537 | 8.1571 | 8.7087 | 8.7087 | 9.2604 | 10.9154 | 11.4671 | 12.5704 | 13.1221 | 13.1221 | 12.5704 | 11.4671 | 10.9154 | 9.8121 | 8.7087 | 8.1571 | 8.1571 | 7.6054 | 9
9 | 58 | 6.2194 | 6.6822 | 6.2194 | 6.2194 | 6.2194 | 6.6822 | 7.145 | 8.0706 | 8.5334 | 8.5334 | 8.9962 | 10.3846 | 10.8474 | 11.7729 | 12.2357 | 12.2357 | 11.7729 | 10.8474 | 10.3846 | 9.459 | 8.5334 | 8.0706 | 8.0706 | 7.6078
9 | 59 | 6.7265 | 7.2896 | 6.7265 | 6.7265 | 6.7265 | 7.2896 | 7.8527 | 8.9788 | 9.5419 | 9.5419 | 10.105 | 11.7942 | 12.3573 | 13.4835 | 14.0466 | 14.0466 | 13.4835 | 12.3573 | 11.7942 | 10.6681 | 9.5419 | 8.9788 | 8.9788 | 8.4158 | 9
9 | 60 | 6.2194 | 6.6822 | 6.2194 | 6.2194 | 6.2194 | 6.6822 | 7.145 | 8.0706 | 8.5334 | 8.5334 | 8.9962 | 10.3846 | 10.8474 | 11.7729 | 12.2357 | 12.2357 | 11.7729 | 10.8474 | 10.3846 | 9.459 | 8.5334 | 8.0706 | 8.0706 | 7.6078
9 | 61 | 8.3823 | 8.9697 | 8.3823 | 8.3823 | 8.3823 | 8.9697 | 9.5571 | 10.732 | 11.3194 | 11.3194 | 11.9069 | 13.6692 | 14.2566 | 15.4314 | 16.0189 | 16.0189 | 15.4314 | 14.2566 | 13.6692 | 12.4943 | 11.3194 | 10.732 | 10.732 | 10.1446 | 9
9 | 62 | 6.2194 | 6.6822 | 6.2194 | 6.2194 | 6.2194 | 6.6822 | 7.145 | 8.0706 | 8.5334 | 8.5334 | 8.9962 | 10.3846 | 10.8474 | 11.7729 | 12.2357 | 12.2357 | 11.7729 | 10.8474 | 10.3846 | 9.459 | 8.5334 | 8.0706 | 8.0706 | 7.6078
9 | 63 | 10.038 | 10.6498 | 10.038 | 10.038 | 10.038 | 10.6498 | 11.2616 | 12.4852 | 13.0969 | 13.0969 | 13.7087 | 15.5441 | 16.1558 | 17.3794 | 17.9912 | 17.9912 | 17.3794 | 16.1558 | 15.5441 | 14.3205 | 13.0969 | 12.4852 | 12.4852 | 11.8734 | 9
10 | 64 | 20.5996 | 20.5996 | 20.5996 | 21.2357 | 21.8719 | 23.1441 | 23.7802 | 24.4164 | 25.6886 | 26.3248 | 26.9609 | 27.597 | 28.2331 | 28.2331 | 28.8693 | 28.8693 | 28.8693 | 28.8693 | 28.2331 | 27.597 | 27.597 | 27.597 | 27.597 | 26.3248 | 10
10 | 65 | 24.6116 | 24.6116 | 24.6116 | 25.2967 | 25.9817 | 27.3518 | 28.0369 | 28.722 | 30.0921 | 30.7771 | 31.4622 | 32.1472 | 32.8323 | 32.8323 | 33.5173 | 33.5173 | 33.5173 | 33.5173 | 32.8323 | 32.1472 | 32.1472 | 32.1472 | 32.1472 | 30.7771
10 | 66 | 22.5963 | 22.5963 | 22.5963 | 23.2567 | 23.9172 | 25.2382 | 25.8986 | 26.5591 | 27.8801 | 28.5406 | 29.201 | 29.8615 | 30.522 | 30.522 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 30.522 | 29.8615 | 29.8615 | 29.8615 | 29.8615 | 28.5406 | 10
10 | 67 | 24.5929 | 24.5929 | 24.5929 | 25.2777 | 25.9626 | 27.3322 | 28.017 | 28.7019 | 30.0715 | 30.7564 | 31.4412 | 32.126 | 32.8108 | 32.8108 | 33.4957 | 33.4957 | 33.4957 | 33.4957 | 32.8108 | 32.126 | 32.126 | 32.126 | 32.126 | 30.7564 | 10
10 | 68 | 24.6116 | 24.6116 | 24.6116 | 25.2967 | 25.9817 | 27.3518 | 28.0369 | 28.722 | 30.0921 | 30.7771 | 31.4622 | 32.1472 | 32.8323 | 32.8323 | 33.5173 | 33.5173 | 33.5173 | 33.5173 | 32.8323 | 32.1472 | 32.1472 | 32.1472 | 32.1472 | 30.7771
10 | 69 | 26.6208 | 26.6208 | 26.6208 | 27.3303 | 28.0399 | 29.459 | 30.1685 | 30.8781 | 32.2972 | 33.0068 | 33.7163 | 34.4259 | 35.1354 | 35.1354 | 35.845 | 35.845 | 35.845 | 35.845 | 35.1354 | 34.4259 | 34.4259 | 34.4259 | 34.4259 | 33.0068 | 10
10 | 70 | 28.6486 | 28.6486 | 28.6486 | 29.3829 | 30.1172 | 31.5858 | 32.32 | 33.0543 | 34.5229 | 35.2572 | 35.9915 | 36.7258 | 37.4601 | 37.4601 | 38.1943 | 38.1943 | 38.1943 | 38.1943 | 37.4601 | 36.7258 | 36.7258 | 36.7258 | 36.7258 | 35.2572 | 10
11 | 71 | 42.8207 | 42.0617 | 42.0617 | 42.8207 | 42.8207 | 43.5797 | 45.0978 | 45.8568 | 47.3748 | 48.1338 | 49.6519 | 50.4109 | 49.6519 | 48.8929 | 47.3748 | 47.3748 | 46.6158 | 47.3748 | 47.3748 | 48.1338 | 48.8929 | 48.8929 | 49.6519 | 49.6519 | 11
11 | 72 | 47.0153 | 46.2135 | 46.2135 | 47.0153 | 47.0153 | 47.8171 | 49.4208 | 50.2226 | 51.8262 | 52.628 | 54.2317 | 55.0335 | 54.2317 | 53.4298 | 51.8262 | 51.8262 | 51.0244 | 51.8262 | 51.8262 | 52.628 | 53.4298 | 53.4298 | 54.2317 | 54.2317
11 | 73 | 45.2443 | 44.4605 | 44.4605 | 45.2443 | 45.2443 | 46.028 | 47.5955 | 48.3792 | 49.9467 | 50.7305 | 52.298 | 53.0817 | 52.298 | 51.5142 | 49.9467 | 49.9467 | 49.163 | 49.9467 | 49.9467 | 50.7305 | 51.5142 | 51.5142 | 52.298 | 52.298 | 11
11 | 74 | 47.0153 | 46.2135 | 46.2135 | 47.0153 | 47.0153 | 47.8171 | 49.4208 | 50.2226 | 51.8262 | 52.628 | 54.2317 | 55.0335 | 54.2317 | 53.4298 | 51.8262 | 51.8262 | 51.0244 | 51.8262 | 51.8262 | 52.628 | 53.4298 | 53.4298 | 54.2317 | 54.2317
11 | 75 | 48.4135 | 47.5974 | 47.5974 | 48.4135 | 48.4135 | 49.2296 | 50.8617 | 51.6778 | 53.31 | 54.1261 | 55.7583 | 56.5743 | 55.7583 | 54.9422 | 53.31 | 53.31 | 52.4939 | 53.31 | 53.31 | 54.1261 | 54.9422 | 54.9422 | 55.7583 | 55.7583 | 11
11 | 76 | 47.0153 | 46.2135 | 46.2135 | 47.0153 | 47.0153 | 47.8171 | 49.4208 | 50.2226 | 51.8262 | 52.628 | 54.2317 | 55.0335 | 54.2317 | 53.4298 | 51.8262 | 51.8262 | 51.0244 | 51.8262 | 51.8262 | 52.628 | 53.4298 | 53.4298 | 54.2317 | 54.2317
11 | 77 | 51.5827 | 50.7343 | 50.7343 | 51.5827 | 51.5827 | 52.4311 | 54.128 | 54.9764 | 56.6733 | 57.5217 | 59.2185 | 60.067 | 59.2185 | 58.3701 | 56.6733 | 56.6733 | 55.8248 | 56.6733 | 56.6733 | 57.5217 | 58.3701 | 58.3701 | 59.2185 | 59.2185 | 11
12 | 78 | 69.7249 | 68.8442 | 68.8442 | 69.7249 | 69.7249 | 70.6057 | 72.3672 | 73.248 | 75.0095 | 76.771 | 77.6518 | 77.6518 | 76.771 | 75.8903 | 75.0095 | 74.1287 | 74.1287 | 74.1287 | 74.1287 | 75.0095 | 75.0095 | 75.8903 | 75.0095 | 74.1287 | 12
12 | 79 | 73.5642 | 72.6501 | 72.6501 | 73.5642 | 73.5642 | 74.4784 | 76.3067 | 77.2208 | 79.0491 | 80.8774 | 81.7916 | 81.7916 | 80.8774 | 79.9633 | 79.0491 | 78.135 | 78.135 | 78.135 | 78.135 | 79.0491 | 79.0491 | 79.9633 | 79.0491 | 78.135
12 | 80 | 73.5642 | 72.6501 | 72.6501 | 73.5642 | 73.5642 | 74.4784 | 76.3067 | 77.2208 | 79.0491 | 80.8774 | 81.7916 | 81.7916 | 80.8774 | 79.9633 | 79.0491 | 78.135 | 78.135 | 78.135 | 78.135 | 79.0491 | 79.0491 | 79.9633 | 79.0491 | 78.135
12 | 81 | 73.4439 | 72.5308 | 72.5308 | 73.4439 | 73.4439 | 74.357 | 76.1832 | 77.0963 | 78.9225 | 80.7487 | 81.6618 | 81.6618 | 80.7487 | 79.8356 | 78.9225 | 78.0094 | 78.0094 | 78.0094 | 78.0094 | 78.9225 | 78.9225 | 79.8356 | 78.9225 | 78.0094 | 12
12 | 82 | 74.844 | 73.9187 | 73.9187 | 74.844 | 74.844 | 75.7693 | 77.6198 | 78.5451 | 80.3957 | 82.2462 | 83.1715 | 83.1715 | 82.2462 | 81.321 | 80.3957 | 79.4704 | 79.4704 | 79.4704 | 79.4704 | 80.3957 | 80.3957 | 81.321 | 80.3957 | 79.4704 | 12
12 | 83 | 73.5642 | 72.6501 | 72.6501 | 73.5642 | 73.5642 | 74.4784 | 76.3067 | 77.2208 | 79.0491 | 80.8774 | 81.7916 | 81.7916 | 80.8774 | 79.9633 | 79.0491 | 78.135 | 78.135 | 78.135 | 78.135 | 79.0491 | 79.0491 | 79.9633 | 79.0491 | 78.135
12 | 84 | 76.2441 | 75.3067 | 75.3067 | 76.2441 | 76.2441 | 77.1816 | 79.0565 | 79.9939 | 81.8688 | 83.7437 | 84.6812 | 84.6812 | 83.7437 | 82.8063 | 81.8688 | 80.9314 | 80.9314 | 80.9314 | 80.9314 | 81.8688 | 81.8688 | 82.8063 | 81.8688 | 80.9314 | 12

## Storage
Bus ID | Type | Capacity [MWh] | Power [MW] | Charging η [%] | Disharging η [%] | SOC init [%] | SOC min [%] | SOC max [%] | Existing
11 | Battery | 60 | 20 | 0.9 | 0.88 | 50 | 20 | 80 | 0
56 | Battery | 45 | 10 | 0.92 | 0.9 | 50 | 25 | 75 | 0
35 | H2 | 10 | 10 | 0.5 | - | 50 | 0 | 100 | 0
74 | Battery | 6 | 3 | 0.89 | 0.88 | 50 | 10 | 90 | 0
104 | H2 | 10 | 10 | 0.5 | - | 50 | 0 | 100 | 0

## Synchronous Generators
| Bus ID | [6 empty] | Generic
Parameter | 3 | 7 | 8 | 9 | 10 | 96 | 97 | Thermal | Hydro
Xd | 1.365 | 1.5 | 1.28 | 1.914 | 1.914 | 1.365 | 1.365 | 1 - 2.9 | 0.6 - 1.5
Xq | 0.685 | 0.8 | 0.64 | 0.98 | 0.98 | 0.685 | 0.685 | 1 - 2.3 | 0.4 - 1
Xd' | 0.19 | 0.22 | 0.18 | 0.40165 | 0.40165 | 0.26 | 0.26 | 0.15 - 0.4 | 0.2 - 0.5
Xq' | 0.685 | 0.685 | 0.6165 | 0.98 | 0.98 | 0.685 | 0.685 | 0.3 - 1 | - | Doesn't apply if salient poles
Xd'' | 0.107 | 0.14 | 0.14 | 0.2756 | 0.2756 | 0.16 | 0.16 | 0.12 - 0.25 | 0.15 - 0.35
Xq'' | 0.17 | 0.15 | 0.15 | 0.30577 | 0.30577 | 0.17 | 0.17 | 0.12 - 0.25 | 0.2 - 0.45
Tdo' | 0.1231 | 0.53 | 0.5 | 1.695 | 1.695 | 1.45 | 1.45 | 3 - 10 s | 1.5 - 9 s
Tqo' | 1.25 | 0.5 | 0.52 | 1.25 | 1.25 | 1.25 | 1.25 | 0.5 - 2 s | - | Doesn't apply if salient poles
Tdo'' | 0.0051 | 0.025 | 0.03 | 0.01575 | 0.01575 | 0.05 | 0.05 | 0.02 - 0.05 s | 0.01 - 0.05 s
Tqo'' | 0.035 | 0.05 | 0.052 | 0.03 | 0.03 | 0.035 | 0.035 | 0.02 - 0.05 s | 0.01 - 0.09 s
Ra | 0.00325 | 0.0064 | 0.0056 | 0.00483 | 0.00483 | 0.00325 | 0.00325 | 0.1 - 0.2 | 0.1 - 0.2
Xl | 0.15 | 0.1 | 0.1 | 0.294 | 0.294 | 0.15 | 0.15 | 0.0015 - 0.005 | 0.002 - 0.02
Xq''sat | 0.14011 | 0.13228 | 0.13104 | 0.252 | 0.252 | 0.15272 | 0.15272
Xd''sat | 0.10166 | 0.13 | 0.13 | 0.227 | 0.227 | 0.15202 | 0.15202 | 0.12 - 0.25 | 0.15 - 0.35 | When in doubt use the same value as Xd''
Xqsat | 0.60672 | 0.70858 | 0.56686 | 0.88537 | 0.88537 | 0.60672 | 0.60672
Xq'sat | 0.57784 | 0.60825 | 0.54742 | 0.8702 | 0.8702 | 0.605 | 0.605
Xdsat | 1.2415 | 1.3643 | 1.1642 | 1.7408 | 1.7408 | 1.2415 | 1.2415
Xd'sat | 0.1684 | 0.19499 | 0.15954 | 0.356 | 0.356 | 0.23045 | 0.23045
H [MWs] | [7 empty] | 2-pole -> 2.5 - 6.0 4-pole -> 4.0 - 10.0 | 2.0 - 4.0
Reactance Values are in pu. Time constants are in seconds (s)
In general:
Xd ≥ Xq > Xq' ≥ Xd' > Xq'' ≥ Xd''
Tdo' > Td' > Tdo'' > Td'' > Tkd
Tq0' > Tq' > Tqo'' > Tq''
The Generic values are extracted from -> Kundur, P., Balu, N. J., & Lauby, M. G. (1994). Power system stability and control (Vol. 7). New York: McGraw-hill. Page 153.

## Asynchronous Generators
Size
Parameter [pu] | 1 MW | 2 MW
Rs | 0.015 | 0.011
Lsigma_s | 0.1 | 0.12
Lm | 2.72 | 3.45
Rr | 0.017 | 0.012
Lsigma_r | 0.12 | 0.12
Abad, G., Lopez, J., Rodriguez, M., Marroyo, L., & Iwanski, G. (2011). Doubly fed induction machine: modeling and control for wind energy generation (Vol. 85). John Wiley & Sons.

## Wind Turbines
Type | Pn [MW] | Vn [kV] | p | cosphin | etan [pu] | Ia/In [pu] | R/X [pu] | Class
1 | 0.85 | 0.69 | 2 | 0.91 | 1 | 7 | 0.15 | DFIG (P, Q and slip)
2 | 0.3 | 0.4 | 2 | 1 | 1 | 5 | 0.15 | DFIG (P, Q and slip)

## Customers
| Customers |  | DTs
Bus ID | Normal | Critical | Normal | Critical
6 | 1955 | 98 | 13 | 1
16 | 1251 | 0 | 8 | 0
17 | 1173 | 0 | 8 | 0
18 | 1720 | 0 | 11 | 0
19 | 1564 | 0 | 10 | 0
20 | 1251 | 0 | 8 | 0
22 | 782 | 0 | 5 | 0
23 | 1408 | 141 | 9 | 1
24 | 938 | 141 | 6 | 1
25 | 704 | 84 | 5 | 1
28 | 938 | 141 | 6 | 1
30 | 938 | 94 | 6 | 1
31 | 1564 | 188 | 10 | 2
32 | 1564 | 156 | 10 | 1
33 | 1095 | 0 | 7 | 0
34 | 1720 | 0 | 11 | 0
35 | 2033 | 0 | 13 | 0
36 | 1564 | 0 | 10 | 0
37 | 1564 | 0 | 10 | 0
38 | 2346 | 0 | 15 | 0
39 | 1720 | 0 | 11 | 0
40 | 2346 | 0 | 15 | 0
41 | 1564 | 0 | 10 | 0
43 | 2424 | 0 | 16 | 0
44 | 1642 | 0 | 11 | 0
46 | 3128 | 313 | 20 | 2
47 | 782 | 0 | 5 | 0
49 | 1720 | 344 | 11 | 3
50 | 1720 | 172 | 11 | 2
51 | 782 | 0 | 5 | 0
52 | 782 | 0 | 5 | 0
53 | 626 | 63 | 4 | 1
54 | 1720 | 0 | 11 | 0
55 | 2346 | 235 | 15 | 2
60 | 1564 | 0 | 10 | 0
63 | 782 | 78 | 5 | 1
64 | 391 | 0 | 3 | 0
65 | 156 | 0 | 1 | 0
66 | 156 | 0 | 1 | 0
67 | 391 | 0 | 3 | 0
71 | 235 | 0 | 2 | 0
73 | 235 | 0 | 2 | 0
75 | 391 | 0 | 3 | 0
78 | 782 | 0 | 5 | 0
79 | 391 | 0 | 3 | 0
80 | 391 | 0 | 3 | 0
81 | 391 | 0 | 3 | 0
82 | 235 | 0 | 2 | 0
84 | 626 | 0 | 4 | 0
86 | 391 | 0 | 3 | 0
87 | 469 | 0 | 3 | 0
88 | 391 | 0 | 3 | 0
89 | 391 | 0 | 3 | 0
90 | 860 | 0 | 6 | 0
91 | 1173 | 0 | 8 | 0
92 | 391 | 0 | 3 | 0
93 | 782 | 0 | 5 | 0
94 | 547 | 0 | 4 | 0
95 | 782 | 0 | 5 | 0
98 | 782 | 0 | 5 | 0
99 | 1720 | 0 | 11 | 0
100 | 782 | 0 | 5 | 0
101 | 391 | 0 | 3 | 0
102 | 391 | 0 | 3 | 0
103 | 704 | 0 | 5 | 0
104 | 196 | 0 | 2 | 0
105 | 391 | 0 | 3 | 0
Total | 70025 | 2248 | 461 | 20
| 72273 |  | 481
| 72330 | 57 | 480 | -1
|  | 0.078805 |  | -0.20833

## Failures
Line ID | FR | FD
1 | 0.02 | 10
2 | 0.02 | 14
3 | 0.018 | 12
4 | 0.12 | 19
5 | 0.02 | 19
6 | 0.02 | 5
7 | 0.02 | 5
8 | 0.02 | 18
9 | 0.02 | 14
10 | 0.018 | 17
11 | 0.02 | 13
12 | 0.018 | 15
13 | 0.018 | 16
14 | 0.02 | 18
15 | 0.02 | 7
16 | 0.02 | 8
17 | 0.02 | 5
18 | 0.02 | 18
19 | 0.018 | 18
20 | 0.018 | 13
21 | 0.018 | 17
22 | 0.02 | 10
23 | 0.02 | 12
24 | 0.018 | 14
25 | 0.018 | 11
26 | 0.018 | 13
27 | 0.018 | 16
28 | 0.017 | 14
29 | 0.018 | 14
30 | 0.018 | 14
31 | 0.018 | 15
32 | 0.02 | 10
33 | 0.018 | 17
34 | 0.018 | 10
35 | 0.018 | 17
36 | 0.017 | 7
37 | 0.018 | 5
38 | 0.018 | 13
39 | 0.018 | 6
40 | 0.02 | 12
41 | 0.018 | 15
42 | 0.018 | 13
43 | 0.018 | 15
44 | 0.018 | 13
45 | 0.018 | 18
48 | 0.018 | 16
49 | 0.018 | 8
50 | 0.018 | 14
51 | 0.02 | 12
52 | 0.02 | 15
53 | 0.02 | 16
54 | 0.02 | 20
55 | 0.02 | 5
56 | 0.02 | 14
57 | 0.02 | 8
58 | 0.02 | 19
59 | 0.02 | 15
60 | 0.02 | 15
61 | 0.018 | 13
62 | 0.018 | 13
63 | 0.018 | 8
64 | 0.018 | 20
65 | 0.02 | 11
66 | 0.02 | 10
67 | 0.018 | 7
68 | 0.018 | 9
69 | 0.018 | 14
70 | 0.018 | 19
71 | 0.018 | 16
72 | 0.018 | 7
73 | 0.022 | 20
74 | 0.022 | 7
75 | 0.022 | 10
76 | 0.02 | 10
77 | 0.02 | 13
78 | 0.02 | 11
79 | 0.02 | 20
80 | 0.02 | 18
81 | 0.02 | 14
82 | 0.02 | 8
83 | 0.02 | 20
84 | 0.02 | 9
85 | 0.02 | 20
86 | 0.02 | 18
87 | 0.02 | 9
88 | 0.02 | 14
89 | 0.02 | 17
90 | 0.02 | 6
91 | 0.02 | 18
92 | 0.02 | 9
93 | 0.018 | 9
94 | 0.02 | 11
95 | 0.02 | 16
96 | 0.02 | 14
97 | 0.02 | 7
98 | 0.02 | 15
99 | 0.02 | 20
100 | 0.02 | 13
101 | 0.02 | 17
102 | 0.02 | 20
103 | 0.02 | 20
104 | 0.02 | 16
105 | 0.02 | 20
106 | 0.02 | 18
107 | 0.02 | 5
108 | 0.02 | 20
109 | 0.02 | 19
110 | 0.018 | 13
111 | 0.018 | 19
112 | 0.018 | 10
113 | 0.018 | 15
114 | 0.018 | 15
115 | 0.02 | 13
116 | 0.02 | 14
117 | 0.02 | 10
118 | 0.25 | 7
119 | 0.25 | 11
120 | 0.25 | 12
121 | 0.25 | 17
122 | 0.25 | 16
123 | 0.25 | 17
124 | 0.25 | 9
125 | 0.25 | 9
126 | 0.25 | 10
127 | 0.25 | 6
128 | 0.25 | 10
129 | 0.25 | 12
130 | 0.25 | 12
131 | 0.25 | 18
132 | 0.25 | 18

## Substation Reliability
Element | FR | FD
CB | 0.0066 | 36
DT | 0.02 | 192
Bus | 0.22 | 10

## Outage Scenarios
Time (W, D, H) | Outaged Element | Affected
|  | Bus | Load [kVA] | Customers | Duration [h]
3, 3, 15 | CB | 72, 75 | 0.55556 | 391 | 20
11, 5, 21 | Line 65 | 56, 60 | 4.8889 | 1564 | 11
18, 4, 7 | CB | 99. 100 | 3.5556 | 2502 | 13
23, 2, 23 | Trafo | 70,68-69 | 21.6111 | 15211 | 16 | Reference
41, 1, 22 | Line 82 | 78, 79 | 0.55556 | 1173 | 8
49, 7, 14 | CB | 42, 43 | 5.7778 | 2424 | 36

## GEP
Electra
Number | Type | Size [MVA] | Fuel
| DG |  | Diesel
| WF |  | n/a
| PV |  | n/a
| BESS |  | n/a
BAU
Type | Size [MVA] | Fuel | Year
Optimal
Type | Size [MVA] | Fuel | Year
Green
Type | Size [MVA] | Fuel | Year

## IES
Water Desalination
required m3/year | 7721585
energy kWh/m3 | 3.4838
required avg m3/day | 21155.0274
required kWh/day | 73700.5605
desalination capacity m3/day | 16000 | 15k are from Electra units and 1k are from AdS
Plant Size MW | 2.3 | consistent with the load in bus 6
desalination capacity m3/day | 15000
Plant Size MW | 2.2 | 2.5 MW in bus 6, buses 43 or 46 could host others.
Plant CAPEX €/(m3/day) | 750
New dissalination €/kW | 5250
Demographics
Population CV 2020 | 483621
Population Sao Vicente | 74016
Population Santiago | 269370
Vehicles
Car fleet CV | 72455
Car fleet Sao Vicente | 11089
Car fleet Santiago | 40356
Average car trip km/day | 40 - 45 | for continental Europe, probably lower in CV
Avg EV consumption kWh/km | 5
Emin required kWh/(day*car) | 200
EV Target 2026 % | 25
Public EV targe 2026 % | 30
EV target 2050 % | 100
Ebus fleet CV 2021 | 5
Sao Vicente | 1
Santiago | 4
Ships LH2 | https://www.ship-technology.com/features/hydrogen-vessel/
max speed knots | 15
Cargo capacity tons | 1960
Fuell Cell Size MW | 4
Pnominal MW | 2
LH2 consumption tons/day | 1.3
https://www.energy.gov/sites/prod/files/2019/10/f68/fcto-h2-at-ports-workshop-2019-viii5-ahluwalia.pdf
page 7 smaller, still too big for CV